January 18, 2002

Ms Cynthia Obier

State of Louisiana

Department of Public Safety and Corrections

Office of State Fire Marshal Code Enforcement

 And Building Safety.

5150 Florida Blvd.

Baton Rouge, Louisiana 70806

RE: Camellia Gardens

        P0233508

Dear Ms. Obier

Per our telephone conversation on 4-4-02 we are resubmitting the drawings for approval as a Residential Board and Care Occupancy. This letter is to clarify the type of bldg. we have designed and what is actually being constructed on the site. 

There are a total of six bldg. for this project. Three of the six bldg. are two stories; two of these have Assisted Living Services on the second floor and the first floor are Independent Living services. The other three bldgs. are Independent Living Services and one of them has a kitchen and dining room.

We originally designed the rooms to have firewalls all the way to the roof. The contractor has opted to encapsulate the rooms by having two layers of 5/8” type “X” sheet rock on the ceiling and one layer of 5/8” type “X” on the walls. All corridor halls are encapsulated also. The two story bldg. has a layer of ¾” Gyp. Crete with ¾” plywood on the second floor.

All corridors and apartments are sprinkled. Two of the bldg.’s are sprinkled in the attic that have assembly areas. All corridors and apartments have smoke and fire alarm detection. All apartments have nurse calls.

Please call me with any questions that you may have.

Thank you,

