
SECTION 16121


HEATING CABLES
PART 1 GENERAL

1.1 SUMMARY


A.
Includes But Not Limited To



1.
Furnish and install electric heating cables on roof drain lines as described in Contract Documents and or shown on Electrical Drawings.

PART 2 - PRODUCTS
2.1
COMPONENTS

A.
Electric tracing system consisting of electrical connections, and junction boxes.



1.
Electric Heating Cable

a. Magnesium oxide insulated with copper or resistance alloy conductor and seamless copper sheath where sheath temperatures will not exceed 480(F.

b. Join cable to cold lead‑in section by factory made joint.

c. Each heater factory fabricated to length required.

1) Length required for pipe or equipment to be heated plus an allowance for areas of additional heat loss for valves, flanges, and fittings plus reasonable excess to allow for field variations.

d. Cold lead‑in section shall be seven feet long unless specified otherwise, and be seamless copper sheathed Type M1 cable manufactured by drawing and annealing process.

e. Heating Cables shall be designed for operation on 120 supply voltage.


B.
Control

1. Heating circuits shall be fixed temperature.

2. Thermostat assembly shall be complete with pilot light to indicate ON condition of system.

C. Electrical connections, junction boxes, and necessary acc​essories.


D.
Approved Manufacturers & Models 



1.
Emerson ‑ Chromalox



2.
Equal by Singer

2.2
APPROVED MANUFACTURERS

A.
Emerson


B.
Singer

PART 3  EXECUTION
3.1
INSTALLATION

A.
Install in complete accordance with Manufacturer's recommendations.


B.
Coordinate cable length with job conditions.


END OF SECTION

LDS 557-1804

Orlando Welfare Complex
1
Section 16121

Orlando, Florida
October 11, 2000
Heating Cables


