
SECTION 16138


BOXES
PART 1 GENERAL

1.1 SUMMARY


A.
Includes But Not Limited To



1.
Furnish and install boxes at each outlet location described in Contract Documents.


B.
Related Sections



1.
Section 16100 - General Wiring Methods Requirements

1.2
SYSTEM DESCRIPTION

A.
Boxes shall be accessible and closed with covers or wiring devices and plates.

1.3
SCHEDULING

A.
Coordination - Coordinate installation of floor boxes in carpeted areas with carpet installer to obtain carpet for doors.

PART 2  PRODUCTS
2.1
MATERIALS

A.
Boxes



1.
Galvanized steel, of size to satisfy conditions at each outlet.



2.
Standard 4" (100 mm) square, except boxes for ceiling light fixtures which shall be 4" octagonal, furnished with standard 3/8" (10 mm) fixture studs as required.




a.
Depth of boxes shall be at least 1-1/2" (38 mm).




b.
Boxes installed in glazed tile, concrete, marble, brick, stone and wood walls shall have rectangular sides, square corners without ears, and without plaster rings.




c.
In office millwork, shallower single gang boxes are permitted where mounting depth is re​stricted.



3.
Equipped with plaster ring covers and extensions as required.



4.
Boxes indicated as weatherproof shall be cast type with gasketed covers or devices and plates.


B.
Floor Boxes



1.
Combination Duplex receptacle, telephone outlet and data box with recessed access plate carpeted access door.




a.
Provide duplex receptacle and mounting accessories for each outlet shown on Drawings.




b.
Provide telephone jack and mounting brackets where shown on Drawings.




c.
Provide blank cover plates for unused components.



2.
Approved Manufacturers & Models 




a.
Hubbell 3SFBSS




b.
Steel City 664-S


C.
Thru-the-wall boxes are not allowed.

PART 3  EXECUTION
3.1
PREPARATION

A.
Prior to rough‑in, locations of boxes shall be verified with work of other Trades to insure that they are properly located for purpose intended.


B.
Particular attention shall be paid to boxes which are adjacent to or above millwork items.  Discrepancies shall be reported to Architect prior to rough‑in.

 3.2
INSTALLATION

A.
Mount boxes with rigid steel bar hangers.


B.
Remove knockouts in boxes for entering conduits only.


C.
Install boxes flush or not more than 1/4" (6 mm) back of finished surfaces and level and plumb.


D.
Boxes for switches at door locations shall generally be ins​talled on latch side of door. Door swings shown on electrical drawings shall be verified with architectural drawings, and discrepancies reported to Architect prior to rough‑in.


E.
Arrange boxes for ceiling light fixtures symmetrically with respect to room dimensions and/or structural features.


F.
Center boxes located in walls with respect to doors, panels, furring, trim and consistent with architectural details.


END OF SECTION

LDS 557-1804

Orlando Welfare Complex
1
Section 16138

Orlando, Florida
October 11, 2000
Boxes


