Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

May 13, 2010

Electrical Inspector

1300 Perdido Street

City Hall-Room 7E06

New Orleans, LA  70112

RE:
1620 Martin Luther King Jr. Blvd.


Permit No. 10COM-00570

Dear Sir or Madam:

The wiring from the generator on the one line diagram was inadvertently miss-calculated.  The generator has a 175A circuit breaker that this wiring will be connected to.  The correct  calculation for this wiring is 2/0 .

If you have any questions, or require any further information, please feel free to call.

Sincerely,

Emmett G. Dammon, PE   

