Good afternoon Jason,

Couple of things. Just quick questions.

1. 1.                   Mechanical Rooms on First and Third do not have Prox Readers where they do on the Second and Fourth Floor. Is this right? The proximity reader for the 2nd floor is for the elevator closet and not the mechanical room.  The one shown on the ASI 02 drawings at the 4th floor was deleted per the attached RFI and you provided pricing for this.  A change order will be forthcoming to formally remove this proximity reader.
2. 2.                   Doors C2225, C2108, and C3109A don’t show to have Prox Readers on these doors per plan but they ask for them in the spec’s. Were these part of the change that took effect?  My bid documents, dated May 18th, show proximity readers on the special systems plans.  Are you looking at the correct drawings?
3. 3.                   Door C1000A, Plans show Prox Reader by this door, What am I tying the Access Control into?  Door 1000A is an automatic sliding door, so you would be tying it into the controller for the door.
4. 4.                   Door  C4011, Plans show this door to have a Prox Reader, Hardware Spec’s doesn’t show any electrified hardware.  Prox reader not required per RFI 051 (see note for item 1)
5. 5.                   Door CST2-4 Plans show a Prox Reader but the hardware Spec’s don’t have any electrified hardware to wire to.  Electrified hardware added per RFI 44.
 

I have the floor plans that show the revision to the 4th floor bathrooms ASI No. 5. Can you get me a copy of the original floor plans that don’t show these changes? I need to get the ones that show the door numbers and location of the Prox Readers.  The 4th floor plan that is required was issued in ASI no. 02.  I will send you 3 emails following this one with the drawings attached.  They should also be a part of the CAD files that were sent.
