August 7, 2002

Attn: Dean Born

City Of Slidell

P.O. Box 828

Slidell, LA. 70458

Ref: TMI Building

        430 Old Spanish Trail

         Slidell, LA. 70458

Dear Mr. Born

At our meeting at the job site, the Fire Marshall was questioning if the rear wall with the exit stairs had to be Fire Rated. The answer is no.

This is a new Business Occupancy of less than 50 people.

Travel distance to a Fire Rated stair enclosure at front of Bldg. is approximately 85 ft, to the outside of the building. The rear stair is not a primary exit, meant only for additional fire protection.

Per NFPA 101, Life Safety Code. Section 3.8.2.6 Travel distance of less than 200 ft required.

Per NFPA 101, Life Safety Code. Section 7.2.2.6.3. Separation and Protection of Outside Stairs.

Exception No.2: Outside stairs serving not in excess of two adjacent stories, including the story of exit discharge, shall be permitted to be unprotected where there is a remotely located second exit.

I’m including a cut sheet from the NFPA book. Please call me with any question you may have.

Thank you,

Chuck Dammon 

Vice President & Project Manger

Chuckdammon@yahoo.com
DammonEngineering.com

Cc: Slidell Fire Marshall

      ECO Builders

