Fire Extinguishers shall be conspicuously located where they are readily accessible and immediately available in the event of fire.  

Fire Extinguishers shall be located along normal paths of travel, including exits from areas.

In large rooms, and in certain locations where visual obstructions cannot be completely avoided, means shall be provided to indicate the extinguisher location.

Portable Fire Extinguishers shall be installed using any of the following means:

(1.) Securely on a hanger intended for extinguisher.

(2.) In the bracket supplied by the extinguisher manufacturer.

(3.) In a listed bracket approved for such purpose.

(4.) In cabinets or wall recesses.

Fire Extinguishers having a gross weight not exceeding 40lb shall be installed so that the top of the fire extinguisher is not more than 5 ft above the floor.

Fire Extinguishers having a gross weight greater than 40lb shall be installed so that the top of the fire extinguisher is not more than 3 ½ ft above the floor.

In no case shall the clearance between the bottom of the fire extinguisher and the floor be less than 4 in.

Class A hazards:  Maximum floor area covered by extinguisher: Light Hazard 3,000 ft2, Moderate Hazard 1,500 ft2, Extra Hazard 1,000 ft2, travel distance for of these hazards is limited to 75 feet. 

Travel distances for Class B hazards:

Light 

5-B Extinguisher – 30 ft





10-B Extinguisher – 50 ft



Ordinary
10-B Extinguisher – 30 ft





20-B Extinguisher – 50 ft



Extra

40-B Extinguisher – 30 ft





80-B Extinguisher – 50 ft

