Additional  Comments not covered by CLA Review:

Question about all of the paging systems.  Do the speakers get wired back to the Access Control Room or do they get directly connected to the amplifier sitting on the reception desk?  If back to the Access Control Room, the microphone you have in the package can have a cable length up to 100 feet in the low-impedance position, however I believe you will need shielded cable. Putting amplifier in Access Control Room. I’ll make a note of the wire requirement.

Building A 1st Floor:

There are 2 PA systems shown on the electrical plans, 1 at the dormitory reception desk and 1 at the nurse station sitting next to the AI Phone System.

You show an AI phone at door HC162a but not the base station at the Nurse Station.

I count 14 exit signs without cameras however you show 13

There are 7 cameras on the electrical plans in the Health Care and 1 camera outside the elevators that do not have a designation “D” or “O”.  My assumption was that these are dome cameras.  Your count for dome cameras, CE-D953, is 8.  Remind me to review this with you because CLA did not comment, I need to clarify that the all of these are dome cameras.

I count 3 faux occupancy, Motion, cameras, Rm A100a, A106 & A117, your count is 2.

Door A171 you show a DPS only however the electrical drawings show a CR as well.

And of course the 9 exterior dome cameras.

Building A 2nd Floor:

Door A264 not on your door list. Should be Mortise Lock VCP 4055 x 626

Building A 3rd  Floor:

Door A302 not on your door list. Should be Mortise Lock VCP 4055 x 626

Building A 4th  Floor:

Door A402 not on your door list. Should be Mortise Lock VCP 4055 x 626

Building A 5th  Floor:

Door A502 not on your door list. Should be Mortise Lock VCP 4055 x 626

These are my input for CLA’s Review::

Door		Comment

HC100b		1.  HC100b is shown as a single door on Architectural Plan.  Electrical Plan shows only 1 reader on door HC100b and nothing on HC100a. Correct this is a single door quantity has been adjusted

2.  Comment for you

HC100a		1.  HC100a is shown as a single door on Architectural Plan.  Electrical Plan shows only 1 reader on door HC100b and nothing on HC100a. Correct this is a single door quantity has been adjusted

HC100c		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

HC161b		1.  The electrical plan shows a pushbutton release at the reception desk for door HC160-a not HC-161b. Wasn’t aware of this. I have made changes on my submittal.

BUILDING A

A104a 		1.  Comment for you. This is a standalone lock. No motion sensor required.

2.  Comment for you Push Button is being supplied and installed by others. We only terminate to it.

A124b 		1.  Comment for you. This is a standalone lock. No motion sensor required.

A104b		The electrical plan does show 2 each readers for this door. You are correct. Schedule has been changed.

A100e 		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

A115a 		1.  Comment for you. His door has been taken out of access control

A108 		1.  Comment for you. Can you send me Submittal #352. I don’t seem to have this.

A113A 		1.  This room is a H/C  double bedroom, don’t know about hardware.

2.  Comment for you. This door originally shown on my schedule as door 113. I have changed it to A113A motion sensor is only required if a Door Position Switch is used. This is a private room the door position is not being monitored

A200b, A200d	1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

A269A 		1.  Room A269 is a standard double bedroom;  Room A213 is a H/C double bedroom.  The electrical plan shows A213 with a 2ea PB, 1ea CR and 2ea Z. A269 is a standalone lock. A213 is actually A213A and does get an electric strike and card reader. Schedule has beem changed for A213A.

A202 		1.  Room A202 is a H/C double bedroom.  The electrical plan shows A202 with 2ea PB, 1ea CR and 2ea Z. Not sure about this door. I’m investigating and will get back to you.

A203a		1.  The plans show this as a lounge.  The electrical plan shows A202 with 2ea PB, 0ea CR and 2ea Z. I don’t believe any of the lounges required access control. They are not on any of the other building lounges.

A213 		1.  See A269A above. A269 is a standalone lock. A213 is actually A213A and does get an electric strike and card reader. Schedule has beem changed for A213A.

A239 		1.  The plans show this as a single H/C bedroom.  The electrical plan shows A239 with 2ea PB, 1ea CR and 2ea Z. Both hardware schedule and my schedule show this door as a standalone lock. Not all H/C rooms are card reader and electric strikes. Not on the second floor and up.

A254a		1.  The plans show this as a lounge.  The electrical plan shows A254 with 2ea PB, 0ea CR and 2ea Z. I don’t believe any of the lounges required access control. They are not on any of the other building lounges.

LUCKY DAY

LD100a		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

LD116, LD118	1. LD116 is an Elevator.  LD118 is an egress from a stairway shown on our plan SEC-C1.  The electrical plan does not show any PB, CR or Z for door LD118. This is one of the doors we discussed recently. I have removed LD116

LD115		1.  LD115 is a double door between the waiting area and the offices.  The electrical plan shows LD115 with 2ea PB, 1ea CR and 2ea Z.  This is one of the doors we discussed recently.

2.  Comment for you. The Door Position Switch is in the exit device. Push Button is being supplied and installed by others. We only terminate to it.

BUILDING B

B100b		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

B100a		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

B128a		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

B103A		1.  B103 is the reception desk with the PA.  Room B130 is an H/C Staff Apt.  The electrical plan shows B130A with 2ea PB, 1ea CR and 2ea Z.  This is one of the doors we discussed recently. I have added B103 to submittal. This door should have a standalone lock on it. I have taken out B130 as B130A is the door for the H/C.

B134A		1.  Comment for you This door was originally on my schedule as A134a. I have moved it and relabeled it A134A for the H/C room.

2.   Comment for you. Private room no motion sensor required

3.   Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

B149A		1. Comment for you. This is an H/C private room. No Exit device (push bar) required. However it is card read in and will require an electric strike to function this door.

2.   Comment for you. Private room no motion sensor required

3.   Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

B126		1.  The plans show this as a lounge.  The electrical plan shows B126 with 2ea PB, 0ea CR and 2ea Z. I don’t believe any of the lounges required access control. They are not on any of the other building lounges.

B200 a / b	1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

B213A		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

B220		1.  The plans show this as a single H/C bedroom.  The electrical plan shows B220 with 2ea PB, 1ea CR and 2ea Z.  This is one of the doors we recently discussed. This door is shown on page 13 of the submittal

B249A		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it.

B253		1. The plans show this as a lounge.  The electrical plan shows B253 with 2ea PB, 0ea CR and 0ea Z.  I don’t believe any of the lounges required access control. They are not on any of the other building lounges.

BUILDING C

C101a		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it

C122b		1.  This is the exterior door to the electrical closet. This is a Persona Exit Device (Card Reader) Because it is an exterior door Door Position Switch is required with Motion Sensor these two items need to be roughed in as they will require hard wiring.

C100a		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it

C125A		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it

C131A		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it

C132A		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it

C200a		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it

C213		1.  Comment for you. Push Button is being supplied and installed by others. We only terminate to it

C320		1.  This is the laundry room. Deleting from Submittal

C420		1.  This is the laundry room. Deleting from Submittal

C520		1.  This is the laundry room. Deleting from Submittal

Building A CCTV

3rd Floor -  	1.  The electrical plans show a faux Smoke Detector with camera outside room A334 and the other one is outside  Room A358.  Your count was for only 1.

4th Floor	1.  The electrical plans show a faux Smoke Detector with camera outside room A434 and the other one is outside  Room A458.  Your count was for only 1.

5th Floor 	1. The electrical plans show a faux Smoke Detector with camera outside room A534 and the other one is outside  Room A558.  Your count was for only 1.

Building B CCTV

1st Floor	1.  I can find only 7 faux Occupancy Sensor Cameras. Correct quantity submittal has ben adjusted.

Building A Paging System

1st Floor	1.  I found 33 speakers on the electrical plans.  It does look like the 2 speakers in the hallway outside HC104 could be combined into one.

2nd Floor	1.  I found 21 speakers on the electrical plans.