Edward C. Gremillion, PE, PLS

P. O. Box 1771

Slidell, LA  70459

(985) 643-3058

January 11, 2005

Dammon Engineering, Inc.

Attention: Mr. Emmett Dammon

1095 Florida Avenue

Slidell, LA  70458

RE:
M.G. Mayor Services, Inc.


332 Bayou Liberty Road


Slidell, LA  70458


New Boat Dock Installation for a 220,000 lb. Marine Travel Hoist and Related 
Construction.

Gentlemen.


Pursuant to your request to determine compliance of actual construction of the new boat dock and related construction in accordance with the contract drawings and specifications as prepared by Thomas E. Pittman, P.E. dated 9/28/2001. Please be advised of the following.

Several field investigations were accomplished, consisting of inspections to identify building materials employed and the taking of actual dimensions.


To aid and convey our findings, Sheets P1 and P2, stamped and dated 10/09/2001 by Thomas E. Pittman, are transmitted herewith indicating our comments and findings of the actual construction noted thereon.  Also enclosed is a copy of the geotechnical investigation by Eustis Engineering, Inc. dated 10/01/2001 as mentioned above.


These comments and findings of individually noted by item numbers herein, and are also cross referenced to the drawings.

Reference Sheet P1

Item 1

The centerline dimension of 30’-0” shown to be the center to center 



dimensions of the runways is actually 31’-4”.


Item 2

The wash down slab shown to be 40’ x 80’ is actually 38’-2” x 78’-0”.


Item 3

The wash down slab as sustained may cracks which may be due to the 



design, improper sub-base material and/or compaction.

Reference Sheet P2


Item 4

Section “A”, Elevation of pile supported concrete hoist runway, indicates 



55’ long 12 Class “B” treated exposed  piles thus 24 piles per Section 



“A1”.

