Fax: (985) 641-5950

FAX NUMBER TRANSMITTED TO:       649-9010
TO:  
Billy Spiers


960-0890

FROM:  David Dammon

Reference:   Generator Sets for Slidell Specialty Hospital

DATE:  July 11, 2005

No of pages including cover sheet:   3

COMMENTS:  

Billy,

We have determined that Slidell Specialty Hospital would need a Type 1 or Type 2 essential electrical system power source as described in NFPA 99.  NFPA 99, para 4.4.1.1.7.1 states that both Type 1 or Type 2  essential electrical system power sources shall be classified as a Type 10, Class X, Level 1 Generator sets per NFPA 110.

NFPA 110 Table 4.1(a) states for a Class X the minimum time in hours is determined by the application, code or user.  NFPA 110 Table 4.1(b) states that Type 10 requires power restoration within 10 seconds.

If the Fire Marshal has some other reference please let us know.

Thank you,

David Dammon

