ST. TAMMANY FIRE PROTECTION DISTRICT NO. 1

FIRE STATION #10

2745 LAKESHORE VISTA BLVD

SLIDELL, LA 70461


Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221323
SANITARY WASTE INTERCEPTORS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Oil interceptors.

2. Sand interceptors.

1.3 DEFINITIONS

Retain definitions remaining after this Section has been edited.

A. FRP: Fiberglass-reinforced plastic.

B. PP: Polypropylene plastic.

1.4 ACTION SUBMITTALS

A. Product Data: For each type of metal or plastic interceptor indicated. Include materials of fabrication, dimensions, rated capacities, retention capacities, operating characteristics, size and location of each pipe connection, furnished specialties, and accessories.

B. Shop Drawings: For each type and size of precast-concrete interceptor indicated.

1. Include materials of construction, dimensions, rated capacities, retention capacities, location and size of each pipe connection, furnished specialties, and accessories.

1.5 INFORMATIONAL SUBMITTALS

A. Coordination Drawings: Interceptors, drawn to scale, on which the following items are shown and coordinated with each other, based on input from Installers of the items involved:

1. Interceptors.

2. Piping connections. Include size, location, and elevation of each.

3. Interface with underground structures and utility services.

1.6 PROJECT CONDITIONS

Retain this article if interruption of existing sanitary or storm sewer service is required.

A. Interruption of Existing Sewer Services: Do not interrupt services to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary sewer services according to requirements indicated:

1. Notify Architect and Owner no fewer than seven days in advance of proposed interruption of service.

2. Do not proceed with interruption of sewer services without Owner's written permission.

PART 2 -  PRODUCTS

2.1 OIL INTERCEPTORS

Indicate on Drawings the number, size, and arrangement of compartments and baffles in oil interceptors in first paragraph below. Delete optional text below and insert name of authority having jurisdiction for interceptors complying with requirements of authorities having jurisdiction. See Editing Instruction No. 3 in the Evaluations.

A. Oil Interceptors: Precast concrete comply with ASTM C 913.

Delete first subparagraph below if interceptors must comply with requirements of authorities having jurisdiction.

1. Basis-of-Design Product: Subject to compliance with requirements, provide SCI PreCast Oil Separator, SCI OWS 750 or comparable product.

2. Include rubber-gasketed joints, vent connections, manholes, compartments or baffles, and piping or openings to retain oil and to permit wastewater flow.

3. Structural Design Loads:

a. Light-Traffic Load: Comply with ASTM C 890, A-8 (ASSHTO HS10-44).

b. Medium-Traffic Load: Comply with ASTM C 890, A-12 (ASSHTO HS15-44).

c. Heavy-Traffic Load: Comply with ASTM C 890, A-16 (ASSHTO HS20-44).

d. Walkway Load: Comply with ASTM C 890, A-03.

4. Steps: Individual FRP steps, FRP ladder, or ASTM A 615/A 615M, deformed, 1/2-inch steel reinforcing rods encased in ASTM D 4101, PP, wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step. Cast or anchor steps into sidewalls at 12- to 16-inch intervals. Omit steps if total depth from floor of interceptor to finished grade is less than 60 inches.

2.2 SAND/SEDIMENT INTERCEPTOR

Sand interceptors in first paragraph below are small and intended for shallow installation in locations such as outdoor showers.

A. Description: Factory-fabricated, cast-iron or steel body and inlet grate; with settlement chamber and removable basket or strainer.

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

Application:  Municipal Water Systems, Wells - Sand and Sediment Interceptor - Z1187, Sand Intercepror - Z1187-SI.

Application:  Maintenance, Parking Garage, Oil Spill Areas - Oil and Sediment Interceptor.

B. Basis-of-Design Product: Subject to compliance with requirements, provide Zurn Plumbing Products Group; Zurn Specification Drainage Products; Z1187SI or comparable product by one of the following:

1. Josam Company.

2. MIFAB, Inc.

3. Smith, Jay R. Mfg. Co.
4. Tyler Pipe, Inc.; Wade Div.
C. Outlet Piping Connection: Hub, hubless, or threaded, unless otherwise indicated.

D. Grate: Cast iron or steel with reinforcement to provide ASTM C 890, A-03, walkway load.

If more than one sand interceptor is required, delete paragraph below and schedule interceptors on Drawings.

E. Capacities and Characteristics:

1. Capacity: 50 GPM

2. Installation Position: Top flush with grade.

2.3 PRECAST-CONCRETE MANHOLE RISERS

Retain this article for manhole risers for underground concrete interceptors to provide access from grade level to interior of interceptors.

A. Precast-Concrete Manhole Risers: ASTM C 478, with rubber-gasket joints.

1. Structural Design Loads:

a. Light-Traffic Load: Comply with ASTM C 890, A-8 (ASSHTO HS10-44).

b. Medium-Traffic Load: Comply with ASTM C 890, A-12 (ASSHTO HS15-44).

c. Heavy-Traffic Load: Comply with ASTM C 890, A-16 (ASSHTO HS20-44).

d. Walkway Load: Comply with ASTM C 890, A-03.

2. Length: From top of underground concrete structure to grade.

3. Riser Sections: 3-inch minimum thickness and 36-inch diameter.

4. Top Section: Eccentric cone, unless otherwise indicated. Include top of cone to match grade ring size.

5. Gaskets: ASTM C 443, rubber.

6. Steps: Individual FRP steps, FRP ladder, or ASTM A 615/A 615M, deformed, 1/2-inch steel reinforcing rods encased in ASTM D 4101, PP or ASTM A 615/A 615M, deformed, 1/2-inch steel reinforcing rods encased in ASTM D 4101, PP, wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step. Cast or anchor steps into sidewalls at 12- to 16-inch intervals. Steps are not required if total depth from floor of interceptor to finished grade is less than 60 inches.
PART 3 -  EXECUTION

3.1 EARTHWORK

A. Excavating, trenching, and backfilling are specified in Section 02300 "Earth Work."

3.2 INSTALLATION

A. Install precast-concrete interceptors according to ASTM C 891. Set level and plumb.

B. Install manhole risers from top of underground concrete interceptors to manholes and gratings at finished grade.

C. Set tops of manhole frames and covers flush with finished surface in pavements. Set tops 3 inches above finish surface elsewhere, unless otherwise indicated.

D. Set tops of grating frames and grates flush with finished surface.

E. Set interceptors level and plumb.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Make piping connections between interceptors and piping systems.

3.4 IDENTIFICATION

A. Identification materials and installation are specified in Section 02300 "Earth Work." Arrange for installation of green warning tapes directly over piping and at outside edges of underground interceptors.

1. Use warning tapes or detectable warning tape over ferrous piping.

2. Use detectable warning tape over nonferrous piping and over edges of underground structures.

END OF SECTION 221323
	SANITARY WASTE INTERCEPTORS
	221323 - 4



