Architectural

Architect: Robert Lee Wiltse.

1 - Approval from the State Fire Marshal is required. Please contact the State Fire Marshal’s office at 8181 Independence Boulevard, Baton Rouge, LA 70806, Ph. (225) 925-4920 800-256-5452

2- New curb cuts require approval from the Department of Public Works. Please contact Mr. Elmer Darwin at (504) 658-8040 

3- Exterior signs require separate permits. Please comply.

4-

5- A signed statement of a Louisiana registered Architect is required in accordance with Section 106.1.of the City of New Orleans amendments to the International Building Code 2006. The statement shall read as follows: ‘These plans have been prepared under my direct supervision and to the best of my knowledge comply with the local Building Codes and regulations. I will (or will not) supervise the work.

6 - Provide a soil boring to verify the foundation design in accordance with the International Building Code 2006 ed. Section 1812.4.2 as amended by the City of New Orleans.

7- Aisles serving as a portion of the exit access in the means of egress system shall comply with the requirements of Section1014.4 of IBC 2006.

8- Signs stating the maximum occupant content shall be conspicuously posted in each area of assembly, or room used for a similar purpose. Signs shall comply with The International Building Code 2006 ed., Arts. 1004.3.

9- Individual glazed areas in hazardous locations shall meet the requirement of Section 2406 for Safety Glazing. International Building code 2006.ed

10- Comply with accessibility requirement Ramps used as a part of a means of egress shall have a running slope not steeper than one unit vertical in 12 units horizontal (8percet slope) in accordance with Section 1010.2 of IBC 2006.

11- Verify that stair riser heights shall be 7 inches maximum and 4 inches minimum. Stair tread depth shall be 11 inches minimum. The riser height shall be measured vertically between the leading edge of adjacent treads in accordance with 1009.3 of IBC 2006.

12- Verify handrail height, measured above stair tread nosing, shall be uniform, not less than 34 inches and not more than 38inches in accordance with Section 1012.2 of International Building Code 2006.

Mechanical

1. Please note that your mechanical plans do not bear a signed statement and seal of a LA Registered mechanical design engineer as required per Section 106.1.1, IBC 2000, New Orleans Amendments. Please submit revised documents for our review.

2. Your mechanical plans as submitted do not indicate required cfm flow rates in required ares, which shall comply related sections of Chapter 4, IMC 2006. Please submit documentation for our review. 

3. Please submit location and installation details for AHUs and CUs. They shall meet the requirements per sections 303, 304, 305,306and 307, IMC 2006. Please submit evidence of compliance.

4. Your plans do not indicate mounting details for pipe and duct supports, which shall meet requirements of section 305, 603, 604, 605 and 606, IMC 2006. Please submit evidence of compliance. 

5. Please submit opening locations for inlet air, exhaust air and vent terminations with respect to roof, windows and property lines. Thease shall comply with sections 401.4, 401.4.1, 401.4.2, 401.4.3, 401.5 and 401.6, IMC 2006.

Electrical

1. Panel Board shall not be installed in clothes closet as shown on plan E-1 as per NEC article 240.24-D. [PLAN E-1]

2. Any Branch circuit feeding Baptism pool shall have GFCI protection as per the National Electrical Code 2005 Sections 680-41, 680-62, & 680-71 [PLAN E-1]

3. In assembly occupancies designed or intended for 100 or more persons, the fixed wiring methods shall be metal raceways, flexible metal raceways, nonmetallic raceways encased in not less than 50 mm (2 in.) of concrete, Type MI, MC, or AC cable containing an insulated equipment grounding conductor sized in accordance with Table 250.122. as per NEC 2005 Article 518.4 (A) [PLANS E1 & E2]

4. All installed electrical wiring shall conform to the requirements of [New Orleans Amendments to the International Building Code 2006edition - articles 101.4.1 , 106.1 , 2701] as amended by the National Electrical Code [NFPA -70] and such other applicable safety codes as enforced by the Safety & Permits [New Orleans Amendments to the International Building Code 2006edition - articles 101.4.1 , 106.1 , 2701] as amended by the National Electrical Code [NFPA -70] [PLANS E1 & E2]

5. If total Electrical work done under this permit is less than $15,000.00 dollars, then please provide an Electrical estimate of this job from an electrician who is licensed with the City of New Orleans [ CLASS-A license [New Orleans Amendments to the International Building Code 2006edition - articles 101.4.1 , 106.1 , 2701]]. The estimate provided shall be written in the following format:a. Written on paper with the letter-head of the electrician or his electrical contracting company.b. Building Permit Number and the location address.c. Actual details of electrical work that will be done under this Building Permit.d. Estimated Bill shall consists of actual cost estimate of Labor and materials.e. Signature, License Number of the electrician, address, phone number and today’s date.Electrician’s estimate shall describe the actual work and not to refer to any plans, in case the plans do not bear wet seals and signed statement of a Louisiana Registered Electrical Engineer.

