SYSTEM DESCRIPTION


This project entails the installation of the required fire alarm equipment and devices at the Safe Harbor (Domestic Violence Shelter). This is a new Residential Board and Care Occupancy. Fire alarm classification is Remote Supervising Station. The building shall meet the criteria set forth in the State Fire Marshal’s (Mr. V. J. Bella) commentary letter of March 19, 2004. 

The new fire alarm control panel shall be a DMP model XR200F. An EST model BPS6 booster power supply shall be provided to power the facilities ADA compliant strobes and horn/strobe units. Alarm initiation shall be via smoke detectors and manual pull stations. The system shall activate all notification appliances on the activation of any alarm initiating device.

All equipment is listed for its intended use.

SEQUENCE OF OPERATION

	
	Activate smoke detector
	Activate manual pull station
	Open, short or ground on field wiring
	Correct condition and reset control panel

	Activate horns and strobes


	X
	X
	
	

	Indicate condition at control panel


	X
	X
	X
	

	Transmit condition to Central Station monitoring
	X
	X
	X
	

	Return control panel to normal


	
	
	
	X


