Tangipahoa Landfill Storm Water Pumping System
May 9, 2008

Three Proposals:

1. Pump from North Pond to Borrow Area

900 gpm @ 6 fps loss 1.25 ft/100 ft

8” pipe 1000 ft.

Total head loss = 46.37 ft.

2. Pump from North Pond to South Pond

8” pipe 1200 ft 950 gpm loss 1.25 ft/100 ft.

Total head loss = 15 ft.


Pump from South Pond to Borrow Area



4” pipe 240 gpm 900 ft. loss 2.9 ft/100 ft.



10” pipe 240 gpm 1200 ft. loss .03 ft/100 ft.



Total head loss = 38 ft.

3. Pump from North Pond to Borrow Area

Pump from South Pond to Borrow Area


8” pipe 950 gpm 1000 ft loss 1.25 ft/100 ft.


Total head loss = 30.22 ft.


10” pipe 1200 gpm 1300 ft. loss 0.59 ft./100 ft.


Total head loss = 26.1 ft.


4” pipe 240 gpm 900 ft loss – 2.9 ft/100 ft.


Total head loss = 37.87 ft.


Total for 8”, 10”, 4” = 94.19 ft.

