Single Duct Terminal Unit Submittal	
		Size	Design Primary Airflow	Static Pressure	NC Levels	
Tag	Model	Unit	Inlet	Outlet
in	Max.
CFM	Min.
CFM	Heat
CFM	Inlet
in wg	Down
in wg	Min.
in wg	Prim
CFM	Rad.	Disch.	
Quantity	Coil Type	Coil Airflow
CFM	KW	EAT
°F	LAT
°F	Volts/Phase	Steps	

VAV-1	35E - CCN	08	08	12x10	743.0	297.0	297.0	1.0	0.3	0.13	743.0	19	19	
1	Electric	297.0	4	55.0	97.56	208V /3Ph	1	

VAV-2	35E - CCN	06	06	12x8	317.0	127.0	127.0	1.0	0.3	0.07	317.0	16	14	
1	Electric	127.0	2	55.0	104.77	208V /3Ph	1	

VAV-3	35E - CCN	05	05	12x8	168.0	100.0	100.0	1.0	0.3	0.02	168.0	<10	<10	
1	Electric	100.0	1.5	55.0	102.4	208V /3Ph	1	

VAV-4	35E - CCN	08	08	12x10	736.0	294.0	294.0	1.0	0.3	0.13	736.0	19	19	
1	Electric	294.0	4	55.0	98.0	208V /3Ph	1	

VAV-5	35E - CCN	06	06	12x8	228.0	100.0	100.0	1.0	0.3	0.04	228.0	12	<10	
1	Electric	100.0	1.5	55.0	102.4	208V /3Ph	1	

VAV-6	35E - CCN	06	06	12x8	376.0	150.0	150.0	1.0	0.3	0.1	376.0	19	16	
1	Electric	150.0	2	55.0	97.14	208V /3Ph	1	

VAV-7	35E - CCN	08	08	12x10	643.0	257.0	257.0	1.0	0.3	0.1	643.0	18	16	
1	Electric	257.0	3.5	55.0	98.04	208V /3Ph	1	

VAV-8	35E - CCN	08	08	12x10	605.0	242.0	242.0	1.0	0.3	0.09	605.0	17	16	
1	Electric	242.0	3.5	55.0	100.71	208V /3Ph	1	

VAV-9	35E - CCN	08	08	12x10	764.0	306.0	306.0	1.0	0.3	0.14	764.0	20	19	
1	Electric	306.0	4	55.0	96.31	208V /3Ph	1	

VAV-10	35E - CCN	07	07	12x10	416.0	200.0	200.0	1.0	0.3	0.07	416.0	16	15	
1	Electric	200.0	3	55.0	102.4	208V /3Ph	1	

Single Duct Terminal Unit Submittal	
		Size	Design Primary Airflow	Static Pressure	NC Levels	
Tag	Model	Unit	Inlet	Outlet
in	Max.
CFM	Min.
CFM	Heat
CFM	Inlet
in wg	Down
in wg	Min.
in wg	Prim
CFM	Rad.	Disch.	
Quantity	Coil Type	Coil Airflow
CFM	KW	EAT
°F	LAT
°F	Volts/Phase	Steps	

VAV-11	35E - CCN	08	08	12x10	678.0	271.0	271.0	1.0	0.3	0.11	678.0	18	18	
1	Electric	271.0	3.5	55.0	95.81	208V /3Ph	1	

VAV-12	35E - CCN	07	07	12x10	376.0	200.0	200.0	1.0	0.3	0.06	376.0	15	15	
1	Electric	200.0	3.5	55.0	110.3	208V /3Ph	1	

VAV-13	35E - CCN	08	08	12x10	621.0	248.0	248.0	1.0	0.3	0.09	621.0	17	16	
1	Electric	248.0	3.5	55.0	99.6	208V /3Ph	1	

VAV-14	35E - CCN	06	06	12x8	316.0	126.0	126.0	1.0	0.3	0.07	316.0	16	14	
1	Electric	126.0	2	55.0	105.16	208V /3Ph	1	

VAV-15	35E - CCN	06	06	12x8	300.0	120.0	120.0	1.0	0.3	0.07	300.0	15	13	
1	Electric	120.0	2	55.0	107.67	208V /3Ph	1	

VAV-16	35E - CCN	06	06	12x8	210.0	100.0	100.0	1.0	0.3	0.03	210.0	11	<10	
1	Electric	100.0	1.5	55.0	102.4	208V /3Ph	1	

Notes:	1.	Room NC levels shown include attenuation transfer functions obtained from tables in ARI Standard 885.	
	2.	Sound data shall be obtained from tests conducted in accordance with ARI Standard 885-98.	
	3.	Selections based upon Carrier as Manufacturer.