May 31, 2002

Attn: Dean Born

City Of Slidell

P.O. Box 828

Slidell, LA. 70458

Ref: TMI Building

        430 Old Spanish Trail

         Slidell, LA. 70458

Dear Mr. Born

At our meeting yesterday at the job site you asked us to provide you with some code analysis for this job. I have calculated the following:

Window Openings: Type VI Unprotected

3-5 ft. from property line allowable openings 20% of wall area.

.20x60x20=240 S.F. allowed

We have 4x 3x5 = 60 S.F.

2HR Floor Separation: W12x16 Beams 4’ on center as opposed to Bar Joist 24” on center.

The W12x16 beams are strong enough for this load.

With this type of construction a two hour floor rating can be accomplished by using U.L. # N711 design. See attached sheets.

Wall Supports:

The contractor will install two 4” pipe columns @ 7’ centers between main columns, on each side of bldg.

Pete Dammon

