SECURITY ALARM SYSTEM SYMBOL SCHEDULE

SAP

SECURITY ALARM SYSTEM CONTROL PANEL. ADEMCO  

MODEL VISTA-40. FURNISH AND INSTALL AT 54” C/L A.F.F. IN THE 1ST FLOOR DATA ROOM. REQUIRES A DEDICATED 120 VOLT A.C. 15 AMP ELECTRICAL CIRCUIT.

KP

SECURITY ALARM SYSTEM BACKLIT CONTROL KEYPAD AND  

DISPLAY. ADEMCO VISTA MODEL 6139. FURNISH AND INSTALL WHERE INDICATED AT 48” C/L A.F.F. REQUIRES A STANDARD SINGLE GANG ELECTRICAL BACKBOX.



SECURITY ALARM SYSTEM EXTERIOR WEATHERPROOF DUAL  

TONE SIREN/STROBE ALARM SIGNAL UNIT IN A STAINLESS STEEL TAMPER PROOF ENCLOSURE. ADEMCO/ATW MODEL NUMBER PR-DS301SET/STL-1. FURNISH AND INSTALL UNDER THE OVERHANG ON THE HWY. 59 SIDE OF THE BUILDING. REQUIRES A STANDARD SINGLE GANG ELECTRICAL BACKBOX.



SECURITY ALARM SYSTEM RECESSED MAGNETIC ALARM  

CONTACT/SWITCH FOR THE BUILDING DOORS. ADEMCO 

V-PLEX MODEL. 4944SN-WH. FURNISH AND INSTALL WHERE INDICATED AT THE TOP OF THE DOOR ON THE LATCH SIDE. REQUIRES A 3/8” HOLE IN THE DOOR CASING.



SECURITY ALARM SYSTEM SURFACE MOUNT MAGNETIC  

ALARM CONTACT/SWITCH FOR THE BUILDING WINDOWS. ADEMCO V-PLEX AUTO SMART MODEL 4939 SN-WH. FURNISH AND INSTALL WHERE INDCATED ON EACH WINDOW.

SECURITY ALARM SYSTEM PIR MOTION DETECTOR. ADEMCO V-PLEX PIR MODEL 998 MX. FURNISH AND INSTALL WHERE INDICATED IN THE CORNER OF THE ROOM AT 7’0” A.F.F. REQUIRES A STANDARD SINGLE GANG ELECTRICAL BACKBOX.

SD

SECURITY ALARM SYSTEM COMBINATION SMOKE AND HEAT  

DETECTOR. ADEMCO V-PLEX MODEL 5192-SDT. FURNISH AND INSTALL ON THE CEILING WHERE INDICATED. DO NOT INSTALL WITHIN 3’0” FROM AN A.H.U. AIR SUPPLY REGISTER. REQUIRES A STANDARD 3” OCTAGON ELECTRICAL BACKBOX AND TEE BAR SUPPORT.

FUTURE CARD ACCESS CONTROL SYSTEM AND MAGNETIC LOCKING SYSTEM FOR THE BUILDING DOORS.

CACP

FUTURE CARD ACCESS CONTROL PANEL. NORTHERN  

COMPUTERS MODEL NO. N-1000-IV. REQUIRES A STANDARD DOUBLE GANG ELECTRICAL BACKBOX AT 54” C/L A.F.F. IN THE 1ST FLOOR DATA ROOM. REQUIRES A DEDICATED 120 V.A.C. 15 AMP. ELECTRICAL CIRCUIT.

CR

FUTURE CARD ACCESS DOOR CONTROL PROXIMITY CARD  

READER. REQUIRES A STANDARD SINGLE GANG ELECTRICAL BACKBOX WHERE INDICATED AT 34” C/L A.F.F.

EX

FUTURE DOOR CONTROL EMERGENCY EXIT BUTTON.  

REQUIRES A STANDARD SINGLE GANG ELECTRICAL BACKBOX WHERE INDICATED AT 48” C/L A.F.F.

MAG

FUTURE DOOR CONTROL ELECTROMAGNETIC DOOR LOCK  

WITH A 1200 LB. HOLDING FORCE. REQUIRES A STANDARD SINGLE GANG ELECTRICAL SWITCHBOX WHERE INDICATED AT THE TOP OF THE DOOR OPENING ON THE LATCH SIDE. 

MLPS

FUTURE DOOR CONTROL MAGNETIC LOCKING SYSTEM  

POWER SUPPLY PROVIDED WITH A STANBY BATTERY POWER SUPPLY. REQUIRES A STANDARD DOUBLE GANG ELECTRICAL SWITCHBOX INSTALLED AT 54” C/L A.F.F. IN THE DATA ROOM. REQUIRES A DEDICATED 120 VOLT A.C. 15 AMP ELECTRICAL CIRCUIT.

JB

SECURITY ALARM AND DOOR CONTROL SYSTEM JUNCTION  

BOX LOCATED ABOVE THE CEILING WHERE INDICATED AND ADJACENT TO THE DOOR. REQUIRES A STANDARD DOUBLE GANG 2-1/8” DEEP ELECTRICAL BOX AND BLANK COVER.

SECURITY ALARM AND FUTURE CARD ACCESS DOOR CONTROL SYSTEM WIRE AND CABLE.

COMTRAN U.L. LISTED NEC TYPE CL3R/CMR CABLE



COMTRAN

TYPE

CAT. NO.

DESCRIPTION

A.

2805


TWO (2) CONDUCTOR NO. 18 AWG.

 




SHIELDED.

B.

2836


TWO (2) CONDUCTOR NO. 16 AWG.

C.

2837


FOUR (4) CONDUCTOR NO. 16 AWG.

D.

2786


FIVE (5) CONDUCTOR NO. 22 AWG.






SHIELDED.
