Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

Mr. Mark Fitzgerald







August 17, 2011

3538 Mimosa Ct


New Orleans LA 70131

(504) 296-9308

RE:
Initial Site Visit 


Marco’s Pizza


Crescent City Pizza

Suites P & Q

2201 Barataria Blvd,

Marrero, LA 700072

Dear Mr. Fitzgerald,

During the initial site visit, the existing demising walls were inspected.  The finished walls were constructed from the floor to the bottom of the beam, directly atop of the demising walls.  The construction did not cover the beam nor did it cover the 8” gap above the beam where the Z channel roofing was supported. The walls were not constructed as a fire rated partition, which requires them to be built from the floor to the roof deck. 

According to the construction drawings for the Barataria Plaza shell, page A-3, the walls were be built according to the following note:  3 5/8” metal studs @ 16” O.C. with Batt Insulation, 5/8” Fire Rated (F.R.) Gypsum wall board (GWB) each side to underside of roof deck and sealed with Fire Rated foam sealer (typical).  This meant that each demising wall was to be constructed to the roof deck.
Marco’s Pizza required for these walls to be constructed as fire partitions according the National Fire Protection Association and the Louisiana State Fire Marshal.

David Dammon

Project Manager

