## La DOTD
La DOTD Hydraulics Manual Excerpt
Return Period |  | Region I |  |  | Region 2 |  |  | Region 3
| a | b | c | a | b | c | a | b | c
2 Year | 2.815 | 0.282 | -0.899 | 2.375 | 0.221 | -0.922 | 2.138 | 0.192 | -0.891
5 Year | 3.536 | 0.33 | -0.851 | 2.976 | 0.251 | -0.865 | 2.701 | 0.22 | -0.847
10 Year | 4.016 | 0.347 | -0.826 | 3.447 | 0.277 | -0.839 | 3.086 | 0.231 | -0.826
25 Year | 4.611 | 0.346 | -0.798 | 4.092 | 0.297 | -0.808 | 3.592 | 0.238 | -0.809
50 Year | 5.097 | 0.351 | -0.783 | 4.64 | 0.318 | -0.791 | 3.934 | 0.227 | -0.794
100 Year | 5.47 | 0.334 | -0.759 | 5.195 | 0.335 | -0.771 | 4.286 | 0.223 | -0.78

## 10 Year
JG Marine Shop
Slidell, La
Drainage Calculations - Modified Rational Method, LDOTD Hydraulics Manual
Predevelopment Condition
10 Year Frequency
Q= CIA |  |  | Factor | Area, sf | Total | mi^2
C | Undeveloped Area |  | 0.2 | 92235 | 18447 | 0.0033085
| Gravel Area |  | 0.25 | 24316 | 6079
| Building/ Parking |  | 0.95 | 28976 | 27527.2
|  |  |  | 145527 | 52053.2
| Weighted C Factor |  | 0.35769
I | Hydraulic Length, L | 316 | feet
| Slope, in %, S | 0.37975 |  |  | 0.0037975
| Runoff Coefficient, C | 0.35769
| Time of Concentration | Tc | 26.0047 | minutes
|  | 9.5308 | 3.1985 | 1.2119
| I, intensity from Region 1 |  | 4.9287
| D | 0.43341
| a | 4.016
| b | 0.347
| c | -0.826
| Area, Acres | 3.3408
| Q10 Flow, cfs | C*I*A | 5.8897 | cfs
| Q10 Predev Flow | 5.8897 | cfs
JG Marine Shop
Slidell, La
Drainage Calculations - Modified Rational Method, LDOTD Hydraulics Manual
Postdevelopment Condition
10 Year Frequency
Q= CIA |  |  | Factor | Area, sf | Total
C | Undeveloped Area |  | 0.2 | 20202 | 4040.4
| Gravel Area |  | 0.25 | 87649 | 21912.25
| Building/ Parking |  | 0.95 | 37676 | 35792.2
|  |  |  | 145527 | 61744.85
| Weighted C Factor |  | 0.42428
I | Hydraulic Length, L | 420 | feet
| Slope, in %, S | 0.56 |  |  | 0.0056034
| Runoff Coefficient, C | 0.42428
| Time of Concentration | Tc | 22.1873 | minutes
|  | 10.6543 | 2.6368 | 1.122
| I, intensity from Region 1 |  | 5.2874
| D | 0.36979
| a | 4.016
| b | 0.347
| c | -0.826
| Area, Acres | 3.3408
| Q10 Flow, cfs | C*I*A | 7.4947 | cfs
| Q10 Postdev Flow | 7.4947 | cfs
| Q10 Allowable Flow- Undeveloped Flow = |  |  | 5.8897 | cfs
JG Marine Shop
Slidell, La
Drainage Calculations - Modified Rational Method, LDOTD Hydraulics Manual
Storage Requirements for a 10 Year Frequency Storm Event
| i = a(D + b) ^c | Max Storage Volume= (D x q) - (.5 x Q10 Allowable Flow x (D + Tc)
q = D x A x C
Storm Duration (D) | Time | i | q, cfs | Max. Storage Volume, cf | Max. Storage Volume, ac-ft
10 | min | 6.9626 | 9.8692 | 234.3221 | 0.0053793
20 | min | 5.5203 | 7.8249 | 1935.7354 | 0.044438
30 | min | 4.6064 | 6.5294 | 2531.9134 | 0.058125
40 | min | 3.9712 | 5.6291 | 2521.8204 | 0.057893
50 | min | 3.502 | 4.964 | 2137.0862 | 0.049061
60 | min | 3.14 | 4.4509 | 1501.4894 | 0.03447
70 | min | 2.8516 | 4.042 | 687.9014 | 0.015792
80 | min | 2.6159 | 3.7079 | -257.6199 | -0.0059142
90 | min | 2.4193 | 3.4293 | -1304.3365 | -0.029944
100 | min | 2.2527 | 3.1931 | -2430.8326 | -0.055804
110 | min | 2.1095 | 2.9901 | -3621.657 | -0.083142
JG Marine Shop
Slidell, La
Detention Area : |  | Detained water surface elevation = |  |  | 44.50 ft
|  | Storage detention required = |  |  | 8,370 c.f.
The existing drive on the East side of the property used by businesses that are North of this project will not be used to detain water during a storm event.
All detained water will be stored in the parking areas that are located to the North, West and South of the new building.
Five sections of the North parking area were averaged and multiplied by the length between those sections. The North parking area will store =
Avg area with sections= |  | 26.93 | s.f. x | 105 | ft =
| 2827.65 | cu. ft. of water above the catch basins
Four sections of the West parking area were averaged and multiplied by the length between those sections. The West parking area will store =
Avg area with sections= |  | 39.93 | s.f. x | 115.75 | ft =
| 4621.8975 | cu. ft. of water above the catch basins
Four sections of the South parking area were averaged and multiplied by the length between those sections. The South parking area will store =
Avg area with sections= |  | 7.44 | s.f. x | 97 | ft =
| 721.68 | cu. ft. of water above the catch basins
There will be 9 catch basins in detention area. The 9 catch basins will detain :
Avg depth of water in catch basin = |  | 3.27 | ft x | 4 | s.f. x
9 | 117.72 | cu. ft. of water above the catch basins
There will be 450 linear feet of 12" round PVC pipe between the catch basins. The PVC pipes will detain @ 85% capacity :
12" round pipe = |  | 0.785 | s.f. x | 450 | l.f. pipe x
0.85 | 300.2625 | cu. ft. of water inside the pipe
Total detention provided = |  | 8589.21 | c.f of water which exceeds the detention required.
JG Marine Shop
Slidell, La
| Discharge End Area Calculations |  | Q=cA(2gh)^1/2 |  |  |  | 12" round pipe = | 0.785 | s.f. x | 495 | lf of pipe = | 388.575 | c.f. Detention
[11 empty] | x 2 sets = | 777.15
| Allowable Run Off, Q | 5.8897 | CFS | per pipe
| Friction Factor, c | 0.98 | [9 empty] | 1501.4894 | c.f. required detention
| Acceleration, g | 32.2 | ft/ft/sec | [6 empty] | 12" PVC pipe |  | 330.2887 | c.f. detention
| Height above Invert, H ft | 1.63 | ft | [6 empty] | 8 CB | 8.44 | 75.96
| End Area, Sq ft | 0.58659 |  |  | 10.2456 |  |  |  |  | North Parking Lot = |  | 2827 | c.f. detention
[10 empty] | NorthWest Parking = |  | 902 | c.f. detention
| Square Inches | 84.4683 | " | [6 empty] | West Parking Lot = |  | 4622 | c.f. detention
| Diameter, Inches | 10.3732 | " | [6 empty] | SouthWest Parking = |  | 251 | c.f. detention
[10 empty] | South Parking Lot = |  | 722 | c.f. detention
| Use 7.63" Diameter Oriface Plate in Terminal CB | [10 empty] | -8228.7593 | c.f. still required detention
[10 empty] | Detention Pond = |  | 988 | c.f. of detention
[7 empty] | 18" round pipe = | 1.9 | s.f. x | 511 | lf of pipe = | 970.9 | c.f. Detention
[7 empty] | Time (Hours) |  | Post Dev Into Pond (10 Year Storm) | Post Dev Out of Pond (10 Year Storm) | Pre Dev (10 Year Storm)
[7 empty] | 0 |  | 0 | 0 | 0
[7 empty] | 0.1 |  | 3
[7 empty] | 0.2 |  | 3.8
[7 empty] | 0.3 |  | 4.24
[7 empty] | 0.4 |  | 4.24
[7 empty] | 0.5 |  | 4.24
[7 empty] | 0.6 |  | 4.24
[7 empty] | 0.7 |  | 4
[7 empty] | 0.8 |  | 3
[7 empty] | 0.9 |  | 2
[7 empty] | 1 |  | 1
[7 empty] | 1.1 |  | 0
1.2
1.3
1.4
1.5
1.6
1.7
1.8
1.9
2
2.1
2.2
2.3
2.4
2.5
2.6
2.7
2.8
2.9
3
3.1
3.2
3.3
3.4
3.5
3.6
3.7
3.8
3.9

## 25 Year
JG Marine Shop
Slidell, La
Drainage Calculations - Modified Rational Method, LaDOTD Hydraulics Manual
Predevelopment Condition
25 Year Frequency
Q= CIA |  |  | Factor | Area, sf | Total | mi^2
C | Undeveloped Area |  | 0.2 | 92235 | 18447 | 0.0033085
| Gravel Area |  | 0.25 | 24316 | 6079
| Building/ Parking |  | 0.95 | 28976 | 27527.2
|  |  |  | 145527 | 52053.2
| Weighted C Factor |  | 0.35769
| Hydraulic Length, L | 336 | feet
| Slope, in %, S | 0.29762 |  |  | 0.0029762
| Runoff Coefficient, C | 0.35769
| Time of Concentration | Tc | 27.9575 | minutes
|  | 9.7626 | 3.1985 | 1.272
I | I, intensity from Region 1 |  | 5.4449
| D | 0.46596
| a | 4.611
| b | 0.346
| c | -0.798
A | Area, Acres | 3.3408
| Q25 Flow, cfs | C*I*A | 6.5065 | cfs
| Q25 Predev Flow | 6.5065 | cfs / 10% reduction = |  | 5.8558
Postdevelopment Condition
25 Year Frequency
Q= CIA |  |  | Factor | Area, sf | Total
C | Undeveloped Area |  | 0.2 | 20202 | 4040.4
| Gravel Area |  | 0.25 | 87649 | 21912.25
| Building/ Parking |  | 0.95 | 37676 | 35792.2
|  |  |  | 145527 | 61744.85
| Weighted C Factor |  | 0.42428
| Hydraulic Length, L | 328 | feet
| Slope, in %, S | 0.56 |  |  | 0.0056034
| Runoff Coefficient, C | 0.42428
| Time of Concentration | Tc | 20.1394 | minutes
|  | 9.6709 | 2.6368 | 1.122
I | I, intensity from Region 1 |  | 6.2605
| D | 0.33566
| a | 4.611
| b | 0.346
| c | -0.798
A | Area, Acres | 3.3408
| Q25 Flow, cfs | C*I*A | 8.8741 | cfs
| Q25 Postdev Flow | 8.8741 | cfs
| Q25 Allowable Flow w/10% Reduction = |  |  | 5.8558 | cfs
JG Marine Shop
Slidell, La
Drainage Calculations - Modified Rational Method, LDOTD Hydraulics Manual
Storage Requirements for a 25 Year Frequency Storm Event
| i = a(D + b) ^c | Max Storage Volume= (D x q) - (.5 x Q10 Allowable Flow x (D + Tc)
q = D x A x C
Storm Duration (D) | Time | i | q, cfs | Max. Storage Volume, cf | Max. Storage Volume, ac-ft
10 | min | 7.8586 | 11.1393 | 1388.8681 | 0.031884
15 | min | 6.9686 | 9.8778 | 2716.9319 | 0.062372
20 | min | 6.2776 | 8.8983 | 3626.4406 | 0.083252
25 | min | 5.7239 | 8.1134 | 4240.2901 | 0.097344
30 | min | 5.2693 | 7.4691 | 4636.0828 | 0.10643
35 | min | 4.8887 | 6.9296 | 4865.509 | 0.1117
40 | min | 4.5649 | 6.4706 | 4964.4898 | 0.11397
45 | min | 4.2857 | 6.0749 | 4958.8641 | 0.11384
50 | min | 4.0423 | 5.7298 | 4867.7577 | 0.11175
55 | min | 3.828 | 5.426 | 4705.6735 | 0.10803
60 | min | 3.6376 | 5.1562 | 4483.8378 | 0.10294
Detention Area : |  | Detained water surface elevation = |  |  | 6.17 ft
|  | Storage detention required = |  |  | 3,213 cf
Section B on Sheet C102 has been measured at |  |  |  | 25.26 | s.f.
The detention area has an effective cross section equal to |  |  |  | 80 | ft
Total detention provided = |  | 2020.8 | c.f of water which exceeds the detention required.
JG Marine Shop
Slidell, La
| Discharge End Area Calculations |  | Q=cA(2gh)^1/2
| Allowable Run Off, Q | 5.8558 | cfs
| Friction Factor, c | 0.98
| Acceleration, g | 32.2 | ft/ft/sec
| Height above Invert, H ft | 0.5 | ft
| End Area | 1.053 | s.f. |  |  | 5.6745
If we want to use smaller sized pipes then take the end area and divide by 3
| Diameter, Inches | 8.0242 | inches
Use (3) three 8" outfall pipes
[6 empty] | Time (Hours) | Post Dev Into Pond (10 Year Storm) | Post Dev Out of Pond (10 Year Storm) | Pre Dev (10 Year Storm)
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0.1 | 3
[6 empty] | 0.2 | 3.8
[6 empty] | 0.3 | 4.24
[6 empty] | 0.4 | 4.24
[6 empty] | 0.5 | 4.24
[6 empty] | 0.6 | 4.24
[6 empty] | 0.7 | 4
[6 empty] | 0.8 | 3
[6 empty] | 0.9 | 2
[6 empty] | 1 | 1
[6 empty] | 1.1 | 0
1.2
1.3
1.4
1.5
1.6
1.7
1.8
1.9
2
2.1
2.2
2.3
2.4
2.5
2.6
2.7
2.8
2.9
3
3.1
3.2
3.3
3.4
3.5
3.6
3.7
3.8
3.9

## 100 Year
JG Marine Shop
Slidell, La
Drainage Calculations - Modified Rational Method, LDOTD Hydraulics Manual
Predevelopment Condition
100 Year Frequency
Q= CIA |  |  | Factor | Area, sf | Total
C | Undeveloped Area |  | 0.2 | 58784 | 11756.8
| Gravel Area |  | 0.25 | 8100 | 2025
| Building/ Parking |  | 0.95 | 15606 | 14825.7
|  |  |  | 82490 | 28607.5
| Weighted C Factor |  | 0.3468
I | Hydraulic Length, L | 316 | feet
| Slope, in %, S | 0.37975 |  |  | 0.0037975
| Runoff Coefficient, C | 0.3468
| Time of Concentration | Tc | 26.9298 | minutes
|  | 9.5308 | 3.3123 | 1.2119
| I, intensity from Region 1 |  | 6.6076
| D | 0.44883
| a | 5.487
| b | 0.334
| c | -0.759
| Area, Acres | 1.8937
| Q100 Flow, cfs | C*I*A | 4.3394 | cfs
| Q100 Predev Flow | 4.3394 | cfs
El Paso Restaurant
200 West Gloria Switch Road
Carencro, Louisiana Lafayette Parish
Drainage Calculations - Modified Rational Method, LDOTD Hydraulics Manual
Postdevelopment Condition
100 Year Frequency
Q= CIA |  |  | Factor | Area, sf | Total
C | Undeveloped Area |  | 0.2 | 25979 | 5195.8
| Gravel Area |  | 0.25 |  | 0
| Building/ Parking |  | 0.95 | 56511 | 53685.45
|  |  |  | 82490 | 58881.25
| Weighted C Factor |  | 0.7138
I | Hydraulic Length, L | 348 | feet
| Slope, in %, S | 0.56
| Runoff Coefficient, C | 0.7138
| Time of Concentration | Tc | 11.4452 | minutes
|  | 9.8978 | 1.4642 | 1.122
| I, intensity from Region 1 |  | 8.9514
| D | 0.19075
| a | 5.487
| b | 0.334
| c | -0.759
| Area, Acres | 1.8937
| Q100 Flow, cfs | C*I*A | 12.0998 | cfs
| Q100 Postdev Flow | 12.0998 | cfs
| Q100 Allowable Flow- Undeveloped Flow = |  |  | 4.3394 | cfs
El Paso Restaurant
200 West Gloria Switch Road
Carencro, Louisiana Lafayette Parish
Drainage Calculations - Modified Rational Method, LDOTD Hydraulics Manual
Storage Requirements
100 Year Frequency
Storm Duration (D) | Time | i | q, cfs | Max. Storage Volume, cf | Max. Storage Volume, ac-ft
10 | min | 9.2764 | 12.5391 | 4731.6643 | 0.10862
20 | min | 7.4586 | 10.082 | 8004.8029 | 0.18377
30 | min | 6.2975 | 8.5125 | 9927.1078 | 0.2279
40 | min | 5.4842 | 7.4132 | 11094.3361 | 0.25469
50 | min | 4.879 | 6.5951 | 11786.261 | 0.27058
60 | min | 4.409 | 5.9598 | 12154.2866 | 0.27902
75 | min | 3.8701 | 5.2313 | 12287.17 | 0.28208
80 | min | 3.7224 | 5.0316 | 12247.2339 | 0.28116
90 | min | 3.4627 | 4.6806 | 12068.9432 | 0.27707
100 | min | 3.2415 | 4.3816 | 11781.3136 | 0.27046
110 | min | 3.0505 | 4.1234 | 11404.4027 | 0.26181