## IMC
ELEVATOR LOBBY, RM # 104
Note: Treat as "Main Entry Lobby, Office"
Vbz = RpPz + Ra Az
Rp = | 5
Pz = | 10 | per | 1000 | ft2 = | 3
Ra = | 0.06
Az = | 300 | ft2
Vbz = | 15 | cfm
************************************************************
ELEVATOR LOBBY, RM # 203
Note: Treat as "Main Entry Lobby, Office"
Vbz = RpPz + Ra Az
Rp = | 5
Pz = | 10 | per | 1000 | ft2 = | 3
Ra = | 0.06
Az = | 300 | ft2
Vbz = | 15 | cfm
************************************************************
ELEVATOR LOBBY, RM # 304
Note: Treat as "Main Entry Lobby, Office"
Vbz = RpPz + Ra Az
Rp = | 5
Pz = | 10 | per | 1000 | ft2 = | 2
Ra = | 0.06
Az = | 200 | ft2
Vbz = | 10 | cfm
************************************************************
Infiltration
Manual N Table 13b
cfm Infiltration per door | [5 empty] | Winter | Summer
Single door no vestibule has an infiltration rate of | [5 empty] | 60 | 30
Number of doors | [6 empty] | 3
Therefore, total Door Infiltration in cfm | [5 empty] | 180 | 90
Required cfm for ventilation (total) = |  |  |  |  | Ref. Vbz, above: |  | 40 | cfm
Door infiltration | [6 empty] | 90 | cfm
|  | Total fresh air |  | 90 | cfm > | 40 | cfm