From:	SBT-22 Facilities Manager, Dave Everett

To:	NAVFAC/ROICC Construction Manager, Paul Mullins

Subj:	Proposed changes; Design Review Comments, ROF Combatant Craft Layout Drawings

Paul,

The below listed comments are provided as the most recent summary of comments and design review suggestions for the planned ROF project.

Parking Area – Drawing referenced C2.1

The parking area islands and landscaping presents a nice, but not necessary feature for the user. Unless LEED motivated, user prefers maximum space utilization and minimum maintenance. Any savings could be directed to clear trees at the SE access, near the Boat Ramp.

Bldg 2440 – Operations Building

- User requests installation of a Cage area (105) roll-up door (approx 6’W by 7’H) that would replace alcove Rear Entry Door (101) and to relocate the Rear Entry Door (101) under the NE stairway or on the NE side, near the Male Showers (112).

- User requests four cameras in Armory (107) area, one directed at entry door(s) and one in each of the three subdivision/caged areas.

- User would like the central area between Entry (102) and Lobby (103) considered as a medical treatment area with various wall mounted medical equipage.

- User requests relocating the Cage access opening to Male Shower (112) from current location to the center wall, adjacent to the male Head (111).

- Concern about a Life Safety Code requirement for additional doors that lead to the corridor on the second floor, affecting rooms 204, 207, 209.

- User concern/request to consider a second door in rooms 205, 208, 210.

- User requests a metal awning over the exterior stairway at the NE end of building 2440.

- User requests surrendering one foot of the 12’ dimension of the River Ops Control Watch (206) to be added to the 39’10-1/8” dimension of the Briefing Area (203).

- User requests inclusion of floor outlets (if not already specified by Mr. Herve Lara), central in each of the divisible areas on the Briefing Room (203).

- User requests dimensions of RTUO (210) follow/mimic dimensions of SITUO (203). Resizing RTUO (210) would make the approx wall dimensions would change to 24’11” by 23’6”.

- User request the 3’ reduction of RTUO (210) be absorbed in RTUO (208) to provide new dimension of 24’11” by 29’-7-3/8”

- User  requests the following room re-designation:

  - SITUO (205) changes to RTUO (205)

  - SITUCO (204) changes to RTUCO (204)

  - RTUO (208) changes to SITUO (208)

  - RTUCO (207) changes to SITUCO (207)

- Consider the corridor (200) alcove area outside River Ops Control Watch (206) as a potential area for shredders, recycle bins, in addition to a common coffee mess area. User requests installed finished counter top, approx 10’ long at a height 36-40” above the floor, with power available for small appliances (20A circuit).

Bldg 2441 – Boat Maintenance/Staging Area

- Consideration for floor drainage. With the possibility of fuel/oil/coolant spills, user concerns are whether the spills can be contained and directed. Reports are that a floor height, open gutter is included in the RFP to address this concern for containment.

- Overhead 110V, Air and Water service connections. Users requests two overhead hose and reel style service stations that can be dropped/pulled down to provide quick turnaround service without trip hazards in the maintenance floor area.

- 110V, Air and Water service connections throughout the staging area and water hose bibs at six locations (2 per elevation) on the exterior of the building

- Floor finish. User recommends a broom finish (not smooth) for some texture/non-slip footfall but also a clear seal coat to minimize absorption of spills and liquids.

- Ensure appropriate outfitting for first aid and AED’s.

- Users requests consideration to incorporate two small Weapons Cleaning Machines, possible located on the outside NW exterior wall.

Bldg 2442

- Print A2.1 indicates 24 interior bollards inside the building. User requests elimination of these bollards due to the high potential for damage to boats, trailers, and vehicles during transport.

- Platform construction.

  - Although final confirmation is uncertain, User believes the width of the platform can be narrowed to 48” unless UFC or higher level reference mandates width at 60”.

  - User preference would be for an open-grate steel deck, running the full length of the building. It is suggested that concrete/cement platforms be located inside the stairway access doors, then transition to steel, open-grate deck/platform.

  - User recommends setting the BOTTOM HEIGHT of the platform/deck walkway at 66”.

  - User questions why there is no conveyance for pedestrian traffic from the platform to the lower building floor area. If needed. The users suggests two 48” stairways, located at a inside point, aligned with the centerline of the exterior stairways.