ST. TAMMANY FIRE PROTECTION DISTRICT NO. 1

NEW TRAINING FACILITY

34780 S. RANGE ROAD 

SLIDELL LA  70460


Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233300
AIR DUCT ACCESSORIES
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Backdraft and pressure relief dampers.

2. Manual volume dampers.

3. Control dampers.

4. Fire dampers.

5. Smoke dampers.

6. Flange connectors.

7. Turning vanes.

8. Duct-mounted access doors.

9. Flexible ducts.

10. Duct accessory hardware.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For duct accessories. Include plans, elevations, sections, details and attachments to other work.

1. Detail duct accessories fabrication and installation in ducts and other construction. Include dimensions, weights, loads, and required clearances; and method of field assembly into duct systems and other construction. Include the following:

a. Special fittings.

b. Manual volume damper installations.

c. Control-damper installations.

d. Fire-damper and smoke-damper installations, including sleeves; and duct-mounted access doors.

e. Wiring Diagrams: For power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see SECTION 016000 "Product Requirements."

2.1 ASSEMBLY DESCRIPTION

A. Comply with NFPA 90A, "Installation of Air Conditioning and Ventilating Systems," and with NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems."

B. Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for acceptable materials, material thicknesses, and duct construction methods unless otherwise indicated. Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

2.2 MATERIALS

A. Galvanized Sheet Steel: Comply with ASTM A 653/A 653M.

1. Galvanized Coating Designation: G90.

2. Exposed-Surface Finish: Mill phosphatized.

B. Stainless-Steel Sheets: Comply with ASTM A 480/A 480M, Type 304, and having a No. 2 finish for concealed ducts and finish for exposed ducts.

C. Aluminum Sheets: Comply with ASTM B 209, Alloy 3003, Temper H14; with mill finish for concealed ducts and standard, 1-side bright finish for exposed ducts.

D. Extruded Aluminum: Comply with ASTM B 221, Alloy 6063, Temper T6.

E. Reinforcement Shapes and Plates: Galvanized-steel reinforcement where installed on galvanized sheet metal ducts; compatible materials for aluminum and stainless-steel ducts.

F. Tie Rods: Galvanized steel, 1/4-inch minimum diameter for lengths 36 inches or less; 3/8-inch minimum diameter for lengths longer than 36 inches.

2.3 BACKDRAFT AND PRESSURE RELIEF DAMPERS

Copy this article and re-edit for each type of backdraft and pressure relief damper.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

1. Air Balance Inc.; a division of Mestek, Inc.

2. American Warming and Ventilating; a division of Mestek, Inc.

3. Cesco Products; a division of Mestek, Inc.

4. Greenheck Fan Corporation.

5. Lloyd Industries, Inc.

6. Nailor Industries Inc.

7. NCA Manufacturing, Inc.

8. Pottorff.

9. Ruskin Company.

10. Vent Products Company, Inc.

B. Description: Gravity balanced.

C. Maximum Air Velocity: 1000 fpm.

D. Maximum System Pressure: 3-inch wg.

E. Frame: Hat-shaped, 0.05-inch- thick stainless steel, with welded corners or mechanically attached and mounting flange.

F. Blades: Multiple single-piece blades, off-center pivoted, maximum 6-inch width, 0.050-inch- thick aluminum sheet with sealed edges.

G. Blade Action: Parallel.

H. Blade Seals: Neoprene, mechanically locked.

I. Blade Axles:

1. Material: Stainless steel.

2. Diameter: 0.20 inch.

J. Tie Bars and Brackets: Aluminum.

K. Return Spring: Adjustable tension.

L. Bearings: Steel ball or synthetic pivot bushings.

M. Accessories:

1. Adjustment device to permit setting for varying differential static pressure.

2. Counterweights and spring-assist kits for vertical airflow installations.

3. Electric actuators.

4. Chain pulls.

Retain one of two "Screen Mounting" subparagraphs below.

5. Screen Mounting: Front mounted in sleeve.

a. Sleeve Thickness: 20 gage minimum.

b. Sleeve Length: 6 inches minimum.

6. Screen Material: Aluminum.

7. Screen Type: Insect.

8. 90-degree stops.

2.4 MANUAL VOLUME DAMPERS

Show dampers on Drawings.

A. Standard, Steel, Manual Volume Dampers:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

a. Air Balance Inc.; a division of Mestek, Inc.

b. American Warming and Ventilating; a division of Mestek, Inc.

c. Flexmaster U.S.A., Inc.

d. McGill AirFlow LLC.

e. Nailor Industries Inc.

f. Pottorff.

g. Ruskin Company.

h. Trox USA Inc.

i. Vent Products Company, Inc.

2. Standard leakage rating, with linkage outside airstream.

3. Suitable for horizontal or vertical applications.

4. Frames:

a. Frame: Hat-shaped, 0.05-inch- thick stainless steel.

b. Mitered and welded corners.

c. Flanges for attaching to walls and flangeless frames for installing in ducts.

5. Blades:

a. Multiple or single blade.

b. Parallel- or opposed-blade design.

c. Stiffen damper blades for stability.

d. Stainless-steel, 0.064 inch thick.

6. Blade Axles: Stainless steel.

7. Bearings:

a. Molded synthetic

b. Dampers in ducts with pressure classes of 3-inch wg or less shall have axles full length of damper blades and bearings at both ends of operating shaft.

8. Tie Bars and Brackets: Galvanized steel.

Retain "Standard, Aluminum, Manual Volume Dampers" Paragraph below for aluminum ducts. Coordinate with "Installation" Article and Section 233113 "Metal Ducts."

B. Standard, Aluminum, Manual Volume Dampers:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

a. Air Balance Inc.; a division of Mestek, Inc.

b. American Warming and Ventilating; a division of Mestek, Inc.

c. McGill AirFlow LLC.

d. Nailor Industries Inc.

e. Pottorff.

f. Ruskin Company.

g. Trox USA Inc.

h. Vent Products Company, Inc.

2. Standard leakage rating, with linkage outside airstream.

3. Suitable for horizontal or vertical applications.

4. Frames: Hat-shaped, 0.10-inch- thick, aluminum sheet channels; frames with flanges for attaching to walls and flangeless frames for installing in ducts.

5. Blades:

a. Multiple or single blade.

b. Parallel- or opposed-blade design.

c. Stiffen damper blades for stability.

Retain "Roll-Formed Aluminum Blades" or "Extruded-Aluminum Blades" Subparagraph below.

d. Roll-Formed Aluminum Blades: 0.10-inch- thick aluminum sheet.

6. Blade Axles: Stainless steel.

7. Bearings:

a. Molded synthetic.

b. Dampers in ducts with pressure classes of 3-inch wg or less shall have axles full length of damper blades and bearings at both ends of operating shaft.

8. Tie Bars and Brackets: Aluminum.

C. Jackshaft:

1. Size: 1-inch diameter.

2. Material: Galvanized-steel pipe rotating within pipe-bearing assembly mounted on supports at each mullion and at each end of multiple-damper assemblies.

3. Length and Number of Mountings: As required to connect linkage of each damper in multiple-damper assembly.

D. Damper Hardware:

1. Zinc-plated, die-cast core with dial and handle made of 3/32-inch- thick zinc-plated steel, and a 3/4-inch hexagon locking nut.

2. Include center hole to suit damper operating-rod size.

3. Include elevated platform for insulated duct mounting.

2.5 CONTROL DAMPERS

Retain this article if motorized volume-control dampers are not specified in Section 230900 "Instrumentation and Control for HVAC."

If multiple control-damper types are required, copy this article and re-edit for each type; assign each type a drawing designation and indicate each type on Drawings.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

1. American Warming and Ventilating; a division of Mestek, Inc.

2. Arrow United Industries; a division of Mestek, Inc.

3. Cesco Products; a division of Mestek, Inc.

4. Greenheck Fan Corporation.

5. Lloyd Industries, Inc.

6. McGill AirFlow LLC.

7. Metal Form Manufacturing, Inc.

8. Nailor Industries Inc.

9. NCA Manufacturing, Inc.

10. Pottorff.

11. Ruskin Company.

12. Vent Products Company, Inc.

13. Young Regulator Company.

B. Frames:

1. Angle shaped.

2. 0.05-inch- thick stainless steel.

3. Interlocking, gusseted corners.

C. Blades:

1. Multiple blade with maximum blade width of 8 inches.

If retaining second option in first subparagraph below, indicate location of each on Drawings.

2. Parallel-blade design.

3. Stainless steel.

4. 0.064 inch thick single skin or 0.0747-inch- thick dual skin.

Retain one of two "Blade Edging" subparagraphs below.

5. Blade Edging: Closed-cell neoprene.

6. Blade Edging: Inflatable seal blade edging, or replaceable rubber seals.

D. Blade Axles: 1/2-inch- diameter; stainless steel; blade-linkage hardware of zinc-plated steel and brass; ends sealed against blade bearings.

1. Operating Temperature Range: From minus 40 to plus 200 deg F.

E. Bearings:

1. Molded synthetic.

2. Dampers in ducts with pressure classes of 3-inch wg or less shall have axles full length of damper blades and bearings at both ends of operating shaft.

3. Thrust bearings at each end of every blade.

2.6 FIRE DAMPERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

1. Air Balance Inc.; a division of Mestek, Inc.

2. Arrow United Industries; a division of Mestek, Inc.

3. Cesco Products; a division of Mestek, Inc.

4. Greenheck Fan Corporation.

5. Nailor Industries Inc.

6. NCA Manufacturing, Inc.

7. Pottorff.

8. Prefco; Perfect Air Control, Inc.

9. Ruskin Company.

10. Vent Products Company, Inc.

11. Ward Industries, Inc.; a division of Hart & Cooley, Inc.

If both types of dampers are required in "Type" Paragraph below, indicate location of each on Drawings.

B. Type: Dynamic; rated and labeled according to UL 555 by an NRTL.

Retain first paragraph below for dynamic fire dampers.

C. Closing rating in ducts up to 4-inch wg static pressure class and minimum 2000-fpm velocity.

If both 1-1/2- and 3-hour ratings are required in "Fire Rating" Paragraph below, indicate location of each rating on Drawings.

D. Fire Rating: 1-1/2 hours.

E. Frame: Curtain type with blades outside airstream except when located behind grille where blades may be inside airstream; fabricated with roll-formed, 0.034-inch- thick galvanized steel; with mitered and interlocking corners.

F. Mounting Sleeve: Factory- or field-installed, galvanized sheet steel.

1. Minimum Thickness: 0.138 inch or 0.39 inch thick, as indicated, and of length to suit application.

2. Exception: Omit sleeve where damper-frame width permits direct attachment of perimeter mounting angles on each side of wall or floor; thickness of damper frame must comply with sleeve requirements.

G. Mounting Orientation: Vertical or horizontal as indicated.

H. Blades: Roll-formed, interlocking, 0.034-inch- thick, galvanized sheet steel. In place of interlocking blades, use full-length, 0.034-inch- thick, galvanized-steel blade connectors.

Not all manufacturers use blade locks for horizontal units.

I. Horizontal Dampers: Include blade lock and stainless-steel closure spring.

Retain one of two "Heat-Responsive Device" paragraphs below. If multiple temperature ratings are required, indicate location of each heat-responsive-device rating on Drawings.

J. Heat-Responsive Device: resettable link and switch package, factory installed, 165 deg F and 212 deg F rated.

2.7 SMOKE DAMPERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

1. Air Balance Inc.; a division of Mestek, Inc.

2. Cesco Products; a division of Mestek, Inc.

3. Greenheck Fan Corporation.

4. Nailor Industries Inc.

5. Pottorff.

6. Ruskin Company.

Manufacturers offer additional features for engineered smoke-control system dampers.

B. General Requirements: Label according to UL 555S by an NRTL.

C. Smoke Detector: Integral, factory wired for single-point connection.

D. Frame: Hat-shaped, 0.094-inch- thick, galvanized sheet steel, with interlocking, gusseted or mechanically attached corners.

Vertical blades are available for special applications.

E. Blades: Roll-formed, horizontal, overlapping, 0.063-inch-thick, galvanized sheet steel.

F. Leakage: Class II.

G. Rated pressure and velocity to exceed design airflow conditions.

H. Mounting Sleeve: Factory-installed, 0.05-inch-thick, galvanized sheet steel; length to suit wall or floor application with factory-furnished silicone calking.

Retain "Damper Motors" Paragraph below if damper actuators are part of smoke-damper assembly and are not specified in Section 230900 "Instrumentation and Control for HVAC."

I. Damper Motors: Modulating or two-position action.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

J. Comply with NEMA designation, temperature rating, service factor, and enclosure type.
1. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Permanent-Split-Capacitor or Shaded-Pole Motors: With oil-immersed and sealed gear trains.

3. Spring-Return Motors: Equip with an integral spiral-spring mechanism where indicated. Enclose entire spring mechanism in a removable housing designed for service or adjustments. Size for running torque rating of 150 in. x lbf and breakaway torque rating of 150 in. x lbf.

4. Outdoor Motors and Motors in Outdoor-Air Intakes: Equip with O-ring gaskets designed to make motors weatherproof. Equip motors with internal heaters to permit normal operation at minus 40 deg F.

5. Nonspring-Return Motors: For dampers larger than 25 sq. ft., size motor for running torque rating of 150 in. x lbf and breakaway torque rating of 300 in. x lbf.

6. Electrical Connection: 115 V, single phase, 60 Hz.

K. Accessories:

Retain applicable features in subparagraphs below.

1. Auxiliary switches for fan control or position indication.

2. Test and reset switches, remote mounted.

2.8 FLANGE CONNECTORS

If permitted by authorities having jurisdiction, flange connectors can substitute for slip-and-drive connections for smoke dampers.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

1. Ductmate Industries, Inc.

2. Nexus PDQ; Division of Shilco Holdings Inc.

3. Ward Industries, Inc.; a division of Hart & Cooley, Inc.

B. Description: Add-on or roll-formed, factory-fabricated, slide-on transverse flange connectors, gaskets, and components.

C. Material: Galvanized steel.

D. Gage and Shape: Match connecting ductwork.

2.9 TURNING VANES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

1. Ductmate Industries, Inc.

2. Duro Dyne Inc.

3. Elgen Manufacturing.

4. METALAIRE, Inc.

5. SEMCO Incorporated.

6. Ward Industries, Inc.; a division of Hart & Cooley, Inc.

Retain "Manufactured Turning Vanes for Metal Ducts" and "Manufactured Turning Vanes for Nonmetal Ducts" paragraphs below for manufactured turning vanes. Delete for turning vanes fabricated by Installer.

B. Manufactured Turning Vanes for Metal Ducts: Curved blades of galvanized sheet steel; support with bars perpendicular to blades set; set into vane runners suitable for duct mounting.

1. Acoustic Turning Vanes: Fabricate airfoil-shaped aluminum extrusions with perforated faces and fibrous-glass fill.

C. Manufactured Turning Vanes for Nonmetal Ducts: Fabricate curved blades of resin-bonded fiberglass with acrylic polymer coating; support with bars perpendicular to blades set; set into vane runners suitable for duct mounting.

D. General Requirements: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible"; Figures 4-3, "Vanes and Vane Runners," and 4-4, "Vane Support in Elbows."

E. Vane Construction: Double wall.

2.10 DUCT-MOUNTED ACCESS DOORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

1. American Warming and Ventilating; a division of Mestek, Inc.

2. Cesco Products; a division of Mestek, Inc.

3. Ductmate Industries, Inc.

4. Elgen Manufacturing.

5. Flexmaster U.S.A., Inc.

6. Greenheck Fan Corporation.

7. McGill AirFlow LLC.

8. Nailor Industries Inc.

9. Pottorff.

10. Ventfabrics, Inc.

11. Ward Industries, Inc.; a division of Hart & Cooley, Inc.

B. Duct-Mounted Access Doors: Fabricate access panels according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible"; Figures 7-2, "Duct Access Doors and Panels," and 7-3, "Access Doors - Round Duct."

1. Door:

a. Double wall, rectangular.

b. Galvanized sheet metal with insulation fill and thickness as indicated for duct pressure class.

c. Vision panel.

d. Hinges and Latches: 1-by-1-inchbutt or piano hinge and cam latches.

e. Fabricate doors airtight and suitable for duct pressure class.

2. Frame: Galvanized sheet steel, with bend-over tabs and foam gaskets.

3. Number of Hinges and Locks:

a. Access Doors Less Than 12 Inches Square: No hinges and two sash locks.

b. Access Doors up to 18 Inches Square: Continuous and two sash locks.

c. Access Doors up to 24 by 48 Inches: Continuous and two compression latches.

d. Access Doors Larger Than 24 by 48 Inches: Four hinges and two compression latches with outside and inside handles.

C. Pressure Relief Access Door:

1. Door and Frame Material: Galvanized sheet steel.

2. Door: Double wall with insulation fill with metal thickness applicable for duct pressure class.

3. Operation: Open outward for positive-pressure ducts and inward for negative-pressure ducts.

Retain first subparagraph below if pressure is not indicated on Drawings.

4. Factory set at 10-inch wg.

5. Doors close when pressures are within set-point range.

6. Hinge: Continuous piano.

7. Latches: Cam.

8. Seal: Neoprene or foam rubber.

9. Insulation Fill: 1-inch- thick, fibrous-glass or polystyrene-foam board.

2.11 FLEXIBLE DUCTS

UL 181 defines two categories of flexible ducts. Ducts listed according to UL 181 must pass all UL 181 tests. Air connectors listed according to UL 181 must pass most, but not all, UL 181 tests and are limited to lengths of 14 feet (4.3 m) or less.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

1. Flexmaster U.S.A., Inc.

2. McGill AirFlow LLC.

3. Ward Industries, Inc.; a division of Hart & Cooley, Inc.

B. Insulated, Flexible Duct: UL 181, Class 1, aluminum laminate and polyester film with latex adhesive supported by helically wound, spring-steel wire; fibrous-glass insulation; aluminized vapor-barrier film.

1. Pressure Rating: 10-inch wg positive and 1.0-inch wg negative.

2. Maximum Air Velocity: 4000 fpm.

3. Temperature Range: Minus 20 to plus 210 deg F.

LEED Prerequisite EA 2 requires that duct insulation R-value comply with ASHRAE/IESNA 90.1-2004 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts."

4. Insulation R-value: Comply with ASHRAE/IESNA 90.1.

C. Flexible Duct Connectors:

1. Clamps: Stainless-steel band with cadmium-plated hex screw to tighten band with a worm-gear action in sizes 3 through 18 inches, to suit duct size.

2. Non-Clamp Connectors: Adhesive plus sheet metal screws.

2.12 DUCT ACCESSORY HARDWARE

A. Instrument Test Holes: Cast iron or cast aluminum to suit duct material, including screw cap and gasket. Size to allow insertion of pitot tube and other testing instruments and of length to suit duct-insulation thickness.

B. Adhesives: High strength, quick setting, neoprene based, waterproof, and resistant to gasoline and grease.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install duct accessories according to applicable details in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for metal ducts and in NAIMA AH116, "Fibrous Glass Duct Construction Standards," for fibrous-glass ducts.

B. Install duct accessories of materials suited to duct materials; use galvanized-steel accessories in galvanized-steel and fibrous-glass ducts, stainless-steel accessories in stainless-steel ducts, and aluminum accessories in aluminum ducts.

LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, in which Section 6.4.3.3.3 - "Shutoff Damper Controls" restricts the use of backdraft dampers and requires control dampers for certain applications. If applying for LEED certification, retain option, in first paragraph below, required by ASHRAE/IESNA 90.1-2004.

C. Install backdraft dampers at inlet of exhaust fans or exhaust ducts as close as possible to exhaust fan unless otherwise indicated.

To minimize duct noise generated by volume dampers, SMACNA recommends locating dampers at least two duct diameters from fittings and as far away as possible from outlets.

D. Install volume dampers at points on supply, return, and exhaust systems where branches extend from larger ducts. Where dampers are installed in ducts having duct liner, install dampers with hat channels of same depth as liner, and terminate liner with nosing at hat channel.

Coordinate subparagraphs below with Section 233113 "Metal Ducts."

1. Install steel volume dampers in steel ducts.

2. Install aluminum volume dampers in aluminum ducts.

E. Set dampers to fully open position before testing, adjusting, and balancing.

F. Install test holes at fan inlets and outlets and elsewhere as indicated.

G. Install fire and smoke dampers according to UL listing.

H. Install duct access doors on sides of ducts to allow for inspecting, adjusting, and maintaining accessories and equipment at the following locations:

1. On both sides of duct coils.

2. Upstream from duct filters.

3. At outdoor-air intakes and mixed-air plenums.

4. At drain pans and seals.

5. Downstream from manual volume dampers, control dampers, backdraft dampers, and equipment.

6. Adjacent to and close enough to fire or smoke dampers, to reset or reinstall fusible links. Access doors for access to fire or smoke dampers having fusible links shall be pressure relief access doors and shall be outward operation for access doors installed upstream from dampers and inward operation for access doors installed downstream from dampers.

7. Control devices requiring inspection.

8. Elsewhere as indicated.

I. Install access doors with swing against duct static pressure.

Sizes in "Access Door Sizes" Paragraph below are from one manufacturer's literature. SMACNA lists only three sizes, 12 by 12 inches (300 by 300 mm), 16 by 20 inches (400 by 500 mm), and 24 by 24 inches (600 by 600 mm), but makes no recommendations for applications. Indicate location and type of each access door on Drawings.

J. Access Door Sizes:

1. One-Hand or Inspection Access: 8 by 5 inches.

2. Two-Hand Access: 12 by 6 inches.

3. Head and Hand Access: 18 by 10 inches.

4. Head and Shoulders Access: 21 by 14 inches.

5. Body Access: 25 by 14 inches.

6. Body plus Ladder Access: 25 by 17 inches.

Coordinate first paragraph below with Section 230553 "Identification for HVAC Piping and Equipment."

K. Label access doors to indicate the purpose of access door.

L. Install flexible connectors to connect ducts to equipment.

Retain first paragraph below to allow use of flexible duct to connect terminal units to metal duct.

M. Connect terminal units to supply ducts with maximum 12-inch lengths of flexible duct. Do not use flexible ducts to change directions.

N. Connect diffusers or light troffer boots to ducts with maximum 60-inch lengths of flexible duct clamped or strapped in place.

O. Connect flexible ducts to metal ducts with adhesive plus sheet metal screws.

P. Install duct test holes where required for testing and balancing purposes.

3.2 FIELD QUALITY CONTROL

A. Tests and Inspections:

1. Operate dampers to verify full range of movement.

2. Inspect locations of access doors and verify that purpose of access door can be performed.

3. Operate fire and smoke dampers to verify full range of movement and verify that proper heat-response device is installed.

4. Inspect turning vanes for proper and secure installation.

END OF SECTION 233300
	AIR DUCT ACCESSORIES
	233300 - 1



