December 7, 2001

Eric Giroir

Assistant Director of Permits

City of Slidell

2055 Second Street

Slidell, Louisiana  70458

RE:
Camellia Gardens


Possum Hollow Road

Dear Mr. Giroir:

In response to your letter, dated November 8, 2001, please note the following answers to your questions:

1) U.L. Design No. U501 as specified on drawings show a layer of 5/8 inch sheetrock on each side of a stud wall.  The actual design criteria of design No. U501 conflicts with this showing a 3-hour rated wall design in part of concrete or masonry.

A) We are using UL Design No. U333.  One layer of 5/8” sheetrock on each side of wood stud wall.

2) SBC 704.3 – Tenant Fire Separation

Provide a minimum of 1-hour fire resistance construction between tenant spaces.

A) UL U333, 5/8” sheetrock will be applied on each side of stud walls and two layers 5/8” sheetrock will be applied to bottom of ceiling, which complies with Gypsum Association Fire Test FMFC 172,2-25-72: GA File No. RC2601

3) SBC 705.3 – Fireblocking

Fireblocking shall be provided in all walls and partitions to cut off all concealed draft openings both horizontal and vertical and to form a fire barrier between floors and between the upper floor and the roof space.


A)
This code will be adhered to.

4) SBC Table 700

Openings into the access corridors must be rated a minimum of 20 minutes.


A)
All doors that open into access corridors are fire rated for 20 minutes.

5) SBC 1005.4 – Emergency Egress Openings

Provide emergency egress openings for sleeping rooms in accordance with this section.

A) The smallest egress windows we are using are 7.5 square feet.  Code requires not less that 5.7 square feet.  The opening will measure over 22” high and 20” wide.
6) SBC Table 600 – Floor/Ceiling Construction

Provide a minimum of 1-hour rated construction material for floor/ceiling assemblies.


A)
We are using a UL-L513 Floor System with a supervised fire alarm and sprinkler.
7) SBC Table 600 – Roof/Ceiling Construction

Provide a minimum of 1-hour rated construction material for roof/ceiling assemblies.

A) See Table 500.  This facility is type VI unprotected, sprinkled.  This allows in Table 600 to use type VI unprotected, which requires 0 hours protection for roof/ceiling combination.

8) SBC Table 700 – Exit Access Corridors

All exit access corridors must be protected by a minimum of 1-hour fire resistant construction material.


A)
We are using a UL U333 System and also supervised fire alarm and sprinkler.

9) SBC 2305.2 – Draftstopping

Provide draftstopping in accordance with this section (attics and floor/ceiling assemblies).

A) Where approved sprinklers are provided, draftstopping shall be required for area’s over 9,000 square feet.  All other areas will be draft stopped at 3,000 square feet.

10) SBC 2309.7 – Ventilation of Attic Space

Provide attic ventilation in accordance with this section.


A)
Continuous Ridge vents will be installed on all roofs and the soffits will be vented.
MECHANICAL

1) Need more information on bathroom exhaust, (ductwork, where are they being exhausted to?).

A)
All exhaust fans are ducted to the outside using round metal ductwork.
2) Need more details on units to be installed.

A) Attached please find an isometric sketch of a typical wall-mount air handling unit with integral return.

3) Section 609.1 would prohibit the use of an exit corridor as a return air for adjoining spaces.

A) No exit corridors will be used as part of any return for adjoining spaces.  This will necessitate some additional return air duct and grills in building #1, floors 1 and 2, and an additional corridor only unit on floor 1.  Sketches of these changes are attached.

4) Section 406.1 – Smoke detectors would be required in return ducts in all systems over 2000 CFM.

A)
Smoke detectors will be installed in return ducts of all systems over 2,000 CFM.

5) Section 610.6 – The specific location and installation detail of each fire door, fire damper, ceiling damper and smoke damper shall be shown and properly identified on the building plans by the designer.

A) Specific locations for fire dampers are shown at fire walls and outside air intakes.  There are no smoke dampers, ceiling dampers, or fire doors.

6) Need details on kitchen hood; hood would also have to comply with Section 502-Commercial Hoods.

A)
The kitchen hood is provided by others.  Details to come from them.

PLUMBING:

Sheet P-1 (These items have been approved by Stan Polivick.)

1) Need gate valve in lieu of globe valve at water entry to property.

A)
The drawing has been revised to reflect a gate valve.

2) Main sewer line size to be increased fixture unit load for all buildings is too large for 6” pipe.

A)
The drawing has been revised to reflect an 8” sewer main.

3) Water service needs to be increased in size.

A)
The drawing has been revised to reflect an 8” water main.

Sheet P-2

Trap primers required for floor drains in the rest rooms.

Deep seal traps will be used in lieu of trap primers.

Sheet P-3 thru P-7

1) Underground waste lines for all kitchen sinks shall be 3” as per City Ordinance.

A)
Underground waste lines for all kitchen sinks will be 3”.

2) All cleanouts shown on plans shall be accessible.

A)
All cleanouts will be accessible.

Sheet P-6

1) Condensate drains for cooler and freezer in kitchen not shown.

A) We are waiting on final kitchen drawings for locations, but condensate drains will be connected to waste system.

2) Drain hand sink into grease line.

A)
Hand sink will be drained into greasy waste.

3) All underground waste lines to grease trap shall be a minimum of 3”.

A)
All underground waste lines to the grease trap will be a minimum of 3”.

Sheets P-6 & P-7

1) Floor drains required in laundry rooms (409.4.5)

A)
Floor drains will be located in laundry rooms.

Sheet P-11

1) Underground waste lines for all kitchen sinks shall be 3”.

A)
Underground waste lines for all kitchen sinks will be 3”.

2) Refer to riser drawings R-10 and R-15: Washing machines are not allowed to drain into crosses.

A)
Stack T’s will be used in lieu of crosses on all washing machines.

General:

1) Sizing of gas, sewer and water lines not shown on various drawings.

A)
All call-outs are on drawing P-1.

If you have any questions or require any further information, please feel free to call.

Sincerely,

Chuck Dammon

VP/Project Manager

CKD:clh

Camellia Gardens Page 4 of 1

