April 21, 2003

Mr. Lawrence Delaune

State of Louisiana

Department of Public Safety and Corrections

Office of State Fire Marshal Code Enforcement

 and Building Safety.

5150 Florida Blvd.

Baton Rouge, Louisiana 70806

RE: P0255226

       Discovery Development

Slidell, La. 70458 Joseph St.

Dear Mr. Delaune

I called your office and was informed you were out till Tuesday. This letter is to clarify the information from your letter dated April 15, 2003.

 We have moved the wall and entrance door to the apartments to close off the dead end. It is 17’ from the stairway to the end apartment doors. We feel that this meets the requirements of the sections noted and will not have to provide a sprinkler system for the apartments.

Please let me know if this is an approved layout so I can update the complete set of DWG’s. If you have any questions, or require any further information, please call.

Sincerely,

Chuck Dammon/Project Manager

