August 6, 2002

ARC Mechanical Contractors, inc.

P.O. Box 1157

Chalmette, LA. 7004

Ref: Woodson Jr. High School

       Fire Marshall Meeting/Partial Substantial Completion

Dear James,

Today we meet with The Local Fire Marshal. These Items listed are what needed to satisfy this inspection. 

1. Simplex wants to change a Smoke Detector to a Heat Detector located on the 2nd floor hall. The Fire Marshall is requesting an exemption letter from them.

2. The Fire Marshall has requested a Certificate of Compliance. 

3. The new Fire Alarm Panel needs to have all the proper inspection tags.

4. The maintenance department from the School Board has requested that when the alarm is deactivated it will also turn off the strobe lights.

5.  The existing P.A. system is still hooked up and needs to be removed.

6.  The new P.A. system is operational but the rear panel is not installed.

7. With the new P.A. installed, the proper personal need to be trained to use the new

8. System.     

9. There is still an existing pull station that needs to be removed from the boy’s locker room.

Please call me with any question you may have.

Thank You

Chuck Dammon

Vice President/Project Manager

CC. Nicki Taylor

