Mr. Lawrence Delaune

State of Louisiana

Department of Public Safety and Corrections

Office of State Fire Marshal Code Enforcement

 and Building Safety.

5150 Florida Blvd.

Baton Rouge, Louisiana 70806

RE: Woodson Middle School

        P0213800

        NFPA 101, 1997

Dear Mr. Delaune

This letter is to clarify the information from the Fire Alarm dwg’s submitted to you for approval dated November 13, 2000.

You indicated that there is to be a strobe at each floor level landing in the stairways. These stairways are open on the second floor to the corridor, allowing you to see the Horn/Strobe unit installed in the hall. We are asking you if we can eliminate the extra strobe on the landing of the second floor as we do not feel it is required.

Additionaly there was no alarm unit at this location, prior to starting this project.

Thankyou:

