Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

July 15, 2008

Mr. Steven L. Davis

Office of Public Health

Capital Region 2

7173-A Florida Blvd.

Baton Rouge, LA 70806

Phone # (225) 925-7230

RE: Village Lakes Subdivision Wastewater Pumping Station – Lots 1-147 Located in Village Lakes Subdivision (Single Family Residences)

Dear Mr. Davis,

With regards to subject letter, the following responses are provided:

1. A note has been added to the detail, Duplex Lift Station for 60k GPD Treatment Plant, that the contractor is to set the float elevation for 15 minute cycle time, approximately 5 ft depth per cycle.

2. The force main is now designed for a maximum velocity of 10 feet per second.

3. The detail, Duplex Lift Station for 60k GPD Treatment Plant, has been provided to show a 30-degree minimum slope to the hopper bottom.

4. The detail, Duplex Lift Station for 60k GPD Treatment Plant, has been provided which includes the provision for air displacement through an inverted “J” tube.

5. The detail, Duplex Lift Station for 60k GPD Treatment Plant, has been provided to show the top of the wet well is now at the elevation 55.1 feet.

6. The detail, Duplex Lift Station for 60k GPD Treatment Plant, has been provided which includes pumps, valves, appurtenances, and alarms in the same detail.  

7. The detail, Duplex Lift Station for 60k GPD Treatment Plant, has been provided which includes the wet well access hatch size.

8. The detail, Duplex Lift Station for 60k GPD Treatment Plant, has been provided which includes a separate valve box from the wet well.  Notes have been added to seal electrical connections as well as the valve box.

9. The detail, Duplex Lift Station for 60k GPD Treatment Plant, has been provided to show the new pump is submerged.  Please see attached specifications for the new pump.

10.  The above ground pump has been replaced with pumps inside the wet well; they deliver approximately 200 gpm at 25 ft of head.  Please see attached specification for the new pump as well as a new Lift Station worksheet.

If you have any questions, please feel free to call.

Emmett G. Dammon Jr.

PE 8796 

