Reply to State Fire Marshal Review Letter,

Item #4. NFPA 54:9.4.3.2 gas appliances located on roofs or other elevated locations more than 15 feet in height shall have an inside means of access to the roof complying with NFPA 54:9.4.3.3 and 9.4.3.4


There is an existing permanent internal stairway providing roof access from the 3rd floor.  
Item 5. NFPA 54:9.4.2.2 Locate gas utilization equipment on roof 6-feet minimum from the edge or provide an acceptable 42-in minimum barrier on the exposed side.


The existing parapet and all new structural steel elements bring the barrier height to a total of 42”.

Item 6.  NFPA 37:4.1.4 Outdoor engines and their “weatherproof” housings, if provided, shall be located at least 5 feet from openings in walls and at least 5 feet from structures having combustible walls.


The generators are not within 5 feet of a wall opening and all weatherproof enclosures are constructed of noncombustible materials.  The exterior walls are made of concrete and mortar having a fire resistance rating of greater than 1 hour.

Item 7.  NFPA 110:7.3.1 Provide emergency lighting at the generator location.  

NFPA 110 states that a battery powered emergency light is required if the enclosure that the generator is housed includes walk-in access, these units do not include walk-in access.

Item 8.  NFPA 110:7.7.7 Outdoor generators shall be heated as specified in Section 5.3.3.


Each generator utilize antifreeze protection.

Item 9.  NFPA 37:4.1.3.2 The roof construction beneath and beyond the engine and any oil containment dike shall be noncombustible to a minimum distance of 12”.


The generators are located no closer than 32” from any roof construction.  This system does not include an oil containment dike.

