DAMMON ENGINEERING, INC.
dammonengineering.com
ARCHITECTS




ENGINEERS


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS

1095 Florida Ave.



   P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

April 22, 2009

Mr. John Laudun, Architect

Office of State Fire Marshal

8181 Independence Blvd.

Baton Rouge, LA  70806

RE:
Urgent Care Services LLC Hangar



Airport Rd.



Slidell, LA  70460

Dear Mr. Laudun,

Dammon Engineering has been asked by the owner to take over this project.

As can be seen on the attachment, the hangar has an office built in the interior of the hangar.  The initial design called for a separation between the 2 story office and the hangar walls on all four sides of the office, thereby requiring a two hour rating of all exterior office walls.

We wish to change this setup to have the North and East office walls run to the exterior wall of the hangar, so that the South and West office walls are also the hangar walls, eliminating the requirement for rating these two walls.  (Both rated walls will go from floor to roof.)  The attached drawing reflects the change.

Additionally, we request permission to eliminate the requirement for a one hour rating of the interior stair of the office, as the second floor exit to the exterior stair will now be through a non-rated wall.

Robert Wiltse, Architect #2736 of our office will be the POR.

We appreciate your consideration of this matter.

Sincerely,

Emmett G. (Pete) Dammon

