[image: image1.jpg]


554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

dammonengineering.com

info@dammonengineering.com
[image: image2.png]



January 11, 2016
March 24, 2017
Mr. Brandon Comeaux E.I.,
Region 1 Engineer Intern

OPH – District 1
RE:
Wax Museum Condominiums Class C Swimming Pool

New Orleans, Louisiana 
Mr. Comeaux,

In response to your review letter dated March 21, 2017 regarding concerns about the subject pool plans, the following is provided:

1.  Plans page PL-2.2 does not have an engineer's seal, signature, or date. Please provide this page with an engineer’s seal, signature, and date in the response..

   Response: This page of the plan set is from the manufacture and provided for information only as a large cut sheet.  It is not needed within the scope of work to be accomplished and can be removed from the plan set.
2.  Please provide the surface area and volume of hot tubs and number of living units utilizing them. LAC.51 :XXIV.103.A.Swimming Pool (Pools) .b, "Residential Pool- a residential pool shall be defined as any constructed pool, permanent or non-portable, that is intended for noncommercial use as a swimming pool by not more than five owner families and their guests and that is over 24 inches in depth, has a surface area exceeding 250 square feet and/or a volume over 3,750 gallons. (Residential pools are excluded from the provisions of these regulations.)"
   Response:       

3.  XXXXXXXXXXXXXXPlease clarify on plans that the pools main drain covers if not made of shiny metal that they will have a dark colored circle. LAC. 51 :XXIV.51l.C.3, "The grating of the main drain outlet shall be easily visible. Drains not constructed of shiny metal shall be marked with a dark colored circle."

   Response:  Sheet PL-1.2 note pointing to the main drain has been revised; notes have been added to the cutsheets on sheet PL1-4, detail 2 & 3, to state that the main drain and the skimmer equalization covers are to be white with a black frame around the cover.

4.  Please provide documentation that the surface skimmer equalizer line suction cover is VGBA ANSI/APSP-16 2011.

   Response:  The cut sheet has been updated on sheet PL-1.4, detail 03 to show compliance with ANSI/APSP-16 2011.

5.  Please clarify if the existing mechanical room will have ventilation.
   Response:  The existing mechanical room is to be demolished and the new equipment will be installed on a new equipment pad without shelter.

6.  The surface skimmer equalizer line suction cover is rated for 49 GPM when mounted on the pool all. The pools pump is designed to operate at 110 gpm. The surface skimmers and main drains are able to be valved off. If the main drains were to be valved off the flow rate through one of the surface skimmers would be 55 gpm which is a higher flow rate than what the suction cover is rated for. Please select a equalizer line suction cover that is rated for at least the flow rate which may pass through it.

   Response:  The valve for the main drains has been relocated on Sheet PL-1.4 to show that it will now isolate the entire suction line from the pool pump (for maintenance purposes).  The skimmers can be cut-off to allow the pool to be drained.  Either main drain can handle the entire flow rate of the pump.   

If you have any questions, or require additional information, please feel free to call.

Sincerely,

[image: image3.jpg]‘,\u\umm,





David Dammon, President

Dammon Engineering, Inc.

   8/24/2016
