Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 270526

GROUNDING AND BONDING FOR COMMUNICATIONS SYSTEMS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Grounding conductors.

          - Grounding connectors.

          - Grounding busbars.

          - Grounding rods.

          - Grounding labeling.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - BCT: Bonding conductor for telecommunications.

        - EMT: Electrical metallic tubing.

        - TGB: Telecommunications grounding busbar.

        - TMGB: Telecommunications main grounding busbar.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

      - CLOSEOUT SUBMITTALS

        - Operation and maintenance data.

- PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

      - SYSTEM COMPONENTS

        - Comply with J-STD-607-A.

      - CONDUCTORS

See "Grounding Products" Article in the Evaluations for discussion on alternative conductor materials.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

          - Harger Lightning and Grounding.

          - Panduit Corp.

          - Tyco Electronics Corp.

        - Comply with UL 486A-486B.

        - Insulated Conductors: Stranded copper wire, green or green with yellow stripe insulation, insulated for 600 V, and complying with UL 83.

          - Ground wire for custom-length equipment ground jumpers shall be No. 6 AWG, 19-strand, UL-listed, Type THHN wire.

Retain "Cable Tray Equipment Grounding Wire" Subparagraph below if an equipment grounding conductor is required. If the ground wire serves as the telecommunications bonding backbone, indicate wire size on Drawings.

If cable tray contains electrical power conductors, then NFPA 70, Article 392 "Cable Trays" governs, and the minimum equipment grounding conductor size is No. 4 AWG.

          - Cable Tray Equipment Grounding Wire: No. 8 AWG.

        - Bare Copper Conductors:

          - Solid Conductors: ASTM B 3.

          - Stranded Conductors: ASTM B 8.

          - Tinned Conductors: ASTM B 33.

Sizes and types of conductors in three subparagraphs below are typical examples. 28-kcmil (14.2-sq. mm) bonding cable in "Bonding Cable" Subparagraph is slightly larger than No. 6 AWG.

          - Bonding Cable: 28 kcmils, 14 strands of No. 17 AWG conductor, and 1/4 inch in diameter.

          - Bonding Conductor: No. 4 or No. 6 AWG, stranded conductor.

          - Bonding Jumper: Tinned-copper tape, braided conductors terminated with two-hole copper ferrules; 1-5/8 inches wide and 1/16 inch thick.

      - CONNECTORS

        - Irreversible connectors listed for the purpose. Listed by an NRTL as complying with NFPA 70 for specific types, sizes, and combinations of conductors and other items connected. Comply with UL 486A-486B.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - Burndy; Part of Hubbell Electrical Systems.

          - Chatsworth Products, Inc.

          - Harger Lightning and Grounding.

          - Panduit Corp.

          - Tyco Electronics Corp.

        - Compression Wire Connectors: Crimp-and-compress connectors that bond to the conductor when the connector is compressed around the conductor. Comply with UL 467.

          - Electroplated tinned copper, C and H shaped.

        - Busbar Connectors: Cast silicon bronze, solderless compression or exothermic-type, mechanical connector; with a long barrel and two holes spaced on 5/8 or 1-inch centers for a two-bolt connection to the busbar.

        - Welded Connectors: Exothermic-welding kits of types recommended by kit manufacturer for materials being joined and installation conditions.

      - GROUNDING BUSBARS

Retain this article if size of grounding bus and mounting details are not indicated on Drawings. The default dimension is recommended by BICSI for telecommunications busbar.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - Chatsworth Products, Inc.

          - Harger Lightning and Grounding.

          - Panduit Corp.

Indicate length of TMGB on Drawings.

        - TMGB: Predrilled, wall-mounted, rectangular bars of hard-drawn solid copper, 1/4 by 4 inches in cross section, length as indicated on Drawings. The busbar shall be NRTL listed for use as TMGB and shall comply with J-STD-607-A.

          - Predrilling shall be with holes for use with lugs specified in this Section.

In "Mounting Hardware" Subparagraph below, the minimum required clearance is 2 inches (50 mm). 4 inches (100 mm) is typical in the industry. Indicate busbar length on Drawings.

          - Mounting Hardware: Stand-off brackets that provide a 4-inch.

          - Stand-off insulators for mounting shall be Lexan or PVC. Comply with UL 891 for use in 600-V switchboards, impulse tested at 5000 V.

        - TGB: Predrilled rectangular bars of hard-drawn solid copper, 1/4 by 2 inches in cross section, length as indicated on Drawings. The busbar shall be for wall mounting, shall be NRTL listed as complying with UL 467, and shall comply with J-STD-607-A.

          - Predrilling shall be with holes for use with lugs specified in this Section.

          - Mounting Hardware: Stand-off brackets that provide at least a 2-inch

          - Stand-off insulators for mounting shall be Lexan or PVC. Comply with UL 891 for use in 600-V switchboards, impulse tested at 5000 V.

Retain "Rack and Cabinet Grounding Busbars" Paragraph below if equipment cabinets and racks are not specified with grounding busbars.

        - Rack and Cabinet Grounding Busbars: Rectangular bars of hard-drawn solid copper, accepting conductors ranging from No. 14 to No. 2/0 AWG, NRTL listed as complying with UL 467, and complying with J-STD-607-A. Predrilling shall be with holes for use with lugs specified in this Section.

          - Cabinet-Mounted Busbar: Terminal block, with stainless-steel or copper-plated hardware for attachment to the cabinet.

          - Rack-Mounted Horizontal Busbar: Designed for mounting in 19 or 23-inch   equipment racks. Include a copper splice bar for transitioning to an adjoining rack, and stainless-steel or copper-plated hardware for attachment to the rack.

          - Rack-Mounted Vertical Busbar: 72 or 36 inches stainless-steel or copper-plated hardware for attachment to the rack.

      - GROUND RODS

Retain this article if ground rods incidental to ground rings and duct banks are required. Indicate ground rod locations and connections on Drawings. See "Grounding Products" Article in the Evaluations for discussion on alternative materials.

The installation of grounding electrode system for the alternating-current (ac) power system, which includes ground rods, ground rings, metal underground water pipes, metal building frames, concrete-encased electrodes, and pipe and plate electrodes, is specified in Section 260526 "Grounding and Bonding for Electrical Systems." The grounding and bonding system of this Section is connected to the grounding and bonding of the ac power system with the BCT from the TMBG specified in "Grounding Electrode System" Article.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

          - Harger Lightning and Grounding.

          - Tyco Electronics Corp.

        - Ground Rods: Copper-clad; 5/8 by 96 inches in diameter.

      - LABELING

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

          - Brother International Corporation.

          - HellermannTyton.

          - Panduit Corp.

        - Comply with TIA/EIA-606-A and UL 969 for a system of labeling materials, including label stocks, laminating adhesives, and inks used by label printers.

        - Machine printed, in black, by thermal transfer or equivalent process. Minimum letter height shall be 3/8 inch. Overlay shall provide a weatherproof and UV-resistant seal for label.

- EXECUTION

      - EXAMINATION

See "Ground Resistance" Article in the Evaluations for discussion of ground-resistance levels.

        - Examine the ac grounding electrode system and equipment grounding for compliance with requirements for maximum ground-resistance level and other conditions affecting performance of grounding and bonding of the electrical system.

        - Inspect the test results of the ac grounding system measured at the point of BCT connection.

        - Prepare written report, endorsed by Installer, listing conditions detrimental to performance of the Work.

        - Proceed with connection of the BCT only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Bonding shall include the ac utility power service entrance, the communications cable entrance, and the grounding electrode system. The bonding of these elements shall form a loop so that each element is connected to at least two others.

        - Comply with NECA 1.

        - Comply with J-STD-607-A.

      - APPLICATION

        - Conductors: Install solid conductor for No. 8 AWG and smaller and stranded conductors for No. 6 AWG and larger unless otherwise indicated.

          - The bonding conductors between the TGB and structural steel of steel-frame buildings shall not be smaller than No. 6 AWG.

          - The bonding conductors between the TMGB and structural steel of steel-frame buildings shall not be smaller than No. 6 AWG.

        - Underground Grounding Conductors: Install bare copper conductor, No. 2 AWG minimum.

        - Conductor Terminations and Connections:

          - Pipe and Equipment Grounding Conductor Terminations: Bolted connectors.

          - Underground Connections: Welded connectors except at test wells and as otherwise indicated.

          - Connections to Ground Rods at Test Wells: Bolted connectors.

          - Connections to Structural Steel: Welded connectors.

        - Conductor Support:

          - Secure grounding and bonding conductors at intervals of not less than 36 inches

        - Grounding and Bonding Conductors:

          - Install in the straightest and shortest route between the origination and termination point, and no longer than required. The bend radius shall not be smaller than eight times the diameter of the conductor. No one bend may exceed 90 degrees.

          - Install without splices.

          - Support at not more than 36-inch   intervals.

          - Install grounding and bonding conductors in 3/4-inch   PVC conduit until conduit enters a telecommunications room. The grounding and bonding conductor pathway through a plenum shall be in EMT. Conductors shall not be installed in EMT unless otherwise indicated.

            - If a grounding and bonding conductor is installed in ferrous metallic conduit, bond the conductor to the conduit using a grounding bushing that complies with requirements in Section 270528 "Pathways for Communications Systems," and bond both ends of the conduit to a TGB.

      - GROUNDING ELECTRODE SYSTEM

Retain paragraph below if the size of the BCT between the TMBG and the ac service is not indicated on Drawings. For bonding conductor length up to 52 feet (16 m), use No. 1/0 AWG; if longer, use No. 3/0 AWG. For selection details, see Editing Instruction No. 3 in the Evaluations. The length of the BCT should be less than 30 feet (9 m) because the impedance of this conductor, due to its length, limits its effectiveness.

        - The BCT between the TMBG and the ac service equipment ground shall not be smaller than No. 1/0 AWG.

      - GROUNDING BUSBARS

        - Indicate locations of grounding busbars on Drawings. Install busbars horizontally, on insulated spacers 2 inches minimum from wall, 12 inches above finished floor unless otherwise indicated.

        - Where indicated on both sides of doorways, route bus up to top of door frame, across top of doorway, and down; connect to horizontal bus.

      - CONNECTIONS

        - Bond metallic equipment in a telecommunications equipment room to the grounding busbar in that room, using equipment grounding conductors not smaller than No. 6 AWG.

        - Stacking of conductors under a single bolt is not permitted when connecting to busbars.

        - Assemble the wire connector to the conductor, complying with manufacturer's written instructions and as follows:

          - Use crimping tool and the die specific to the connector.

          - Pretwist the conductor.

          - Apply an antioxidant compound to all bolted and compression connections.

        - Primary Protector: Bond to the TMGB with insulated bonding conductor.

Retain "Interconnections" Paragraph below if all telecommunications backbone and grounding equalizer conductors are not sized on Drawings.

        - Interconnections: Interconnect all TGBs with the TMGB with the telecommunications backbone conductor. If more than one TMGB is installed, interconnect TMGBs using the grounding equalizer conductor. The telecommunications backbone conductor and grounding equalizer conductor size shall not be less than 2 kcmils/linear foot of conductor length, up to a maximum size of No. 3/0 AWG unless otherwise indicated.

        - Telecommunications Enclosures and Equipment Racks: Bond metallic components of enclosures to the telecommunications bonding and grounding system. Install vertically mounted rack grounding busbar unless the enclosure and rack are manufactured with the busbar. Bond the equipment grounding busbar to the TGB No. 2 AWG bonding conductors.

        - Structural Steel: Where the structural steel of a steel frame building is readily accessible within the room or space, bond each TGB and TMGB to the vertical steel of the building frame.

        - Electrical Power Panelboards: Where an electrical panelboard for telecommunications equipment is located in the same room or space, bond each TGB to the ground bar of the panelboard.

Retain "Shielded Cable" Paragraph below if screened twisted-pair cables and coaxial cables are installed in communications equipment rooms.

        - Shielded Cable: Bond the shield of shielded cable to the TGB in communications rooms and spaces. Comply with TIA/EIA-568-B.1 and TIA/EIA-568-B.2 when grounding screened, balanced, twisted-pair cables.

        - Rack- and Cabinet-Mounted Equipment: Bond powered equipment chassis to the cabinet or rack grounding bar. Power connection shall comply with NFPA 70; the equipment grounding conductor in the power cord of cord- and plug-connected equipment shall be considered as a supplement to bonding requirements in this Section.

        - Access Floors: Bond all metal parts of access floors to the TGB.

      - IDENTIFICATION

        - Labels shall be preprinted or computer-printed type.

          - Label TMGB(s) with "fs-TMGB," where "fs" is the telecommunications space identifier for the space containing the TMGB.

          - Label TGB(s) with "fs-TGB," where "fs" is the telecommunications space identifier for the space containing the TGB.

          - Label the BCT and each telecommunications backbone conductor at its attachment point: "WARNING! TELECOMMUNICATIONS BONDING CONDUCTOR. DO NOT REMOVE OR DISCONNECT!"

      - FIELD QUALITY CONTROL

Retain "Perform tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

        - Perform tests and inspections.

Retain "Tests and Inspections" Paragraph below to describe tests and inspections to be performed.

The maximum acceptable connection resistance and ac loop current values are based on recommendations of BICSI TDMM.

        - Tests and Inspections:

          - Inspect physical and mechanical condition. Verify tightness of accessible, bolted, electrical connections with a calibrated torque wrench according to manufacturer's written instructions.

          - Test the bonding connections of the system using an ac earth ground-resistance tester, taking two-point bonding measurements in each telecommunications equipment room containing a TMGB and a TGB and using the process recommended by BICSI TDMM. Conduct tests with the facility in operation.

            - Measure the resistance between the busbar and the nearest available grounding electrode. The maximum acceptable value of this bonding resistance is 100 milliohms.

          - Test for ground loop currents using a digital clamp-on ammeter, with a full-scale of not more than 10 A, displaying current in increments of 0.01 A at an accuracy of plus/minus 2.0 percent.

            - With the grounding infrastructure completed and the communications system electronics operating, measure the current in every conductor connected to the TMGB. Maximum acceptable ac current level is 1 A.

        - Excessive Ground Resistance: If resistance to ground at the BCT exceeds 1 ohms, notify Architect promptly and include recommendations to reduce ground resistance.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Grounding system will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports.

END OF SECTION 27052