ASTM E 1300 GLASS LOAD RESISTANCE REPORT

3/8/2017

JOB DETAILS:

Project Name:		Laurel School Renovation

WINDOW GLASS DETAILS:           1/2 “ Laminated Windows

Lite Support                                    4 Edges

Rectangular Dimensions:	Various

Window Construction:     	 Laminated   -         1/4" CL TP 090 PVB 1/4" CL TP

Window Orientation:		Sloped at 0° from Vertical

G2 Designated Panes from Plans Sheet Numbers 104, 105,  and 106

WINDOW SIZE                                                                                             DEFLECTION

Sheet 104 - Laurel School  G2 - 40.375 x 32.1675                                                       < 0.006”

Sheet 105 - Laurel School  G2 - 40.375 x 31                                                                < 0.006”

Sheet 106 - Laurel School  G2 - 24 x 34.75                                                                   < 0.006”

----------------------------------------------------------------------------------------------------------------------------------

SHORT DURATION LOAD, RESISTANCE AND DEFLECTION DATA:

Load (<=60 sec.)    		                                            :       45 psf

Maximum Allowable Glass Deflection:	:        L/175

CONCLUSION:

The G1 glass configurations are below the maximum L/175 deflection for the specified loading.

STATEMENT OF COMPLIANCE:

Procedures followed in determining the resistance of this window glass configuration are in accordance with ASTM E 1300-97.

Disclaimer:

The load resistance of specified glass types exposed to uniform lateral loads of short or long duration subject to the following conditions:

- The glass is free of edge and surface damage and has been properly glazed in the opening in conformance with the manufacturers recommendations.

- The glass is supported on all sides by a framing system sufficiently stiff to limit lateral deflection of the glass edge (not center-of-glass) less than to 1/175 of the glass edge length; Center of glass deflection in excess of 19-mm (0.75-in.) is a design issue and does not affect glass strength;

- The laminated glass factors for short term loads are representative of roof temperature data to which the glass is exposed.

For other limiting conditions that may apply, refer to Section 5 of ASTM E1300 and local building codes.

Prepared by : 	__________________________	Date:___3/16/2017__________________