## Sheet1
Oxidation Pond Lift Station
Flow gpm |  | Length of 6" HDPE pipe, ft |  |  | Head Loss per 100 Feet of Pipe |  |  | Head Loss
243 |  | 22200 |  |  | 0.4 |  |  | 88.8 | ft
Estimate the Head for valves, bends and other issues | [7 empty] | 15 | ft
There is an elevation difference of | [7 empty] | 16 | ft
[7 empty] | Total | 119.8 | ft
Sewer Grinder Lift Station
60 |  | 7978 |  |  | 0.1 |  |  | 7.978 | ft
Estimate the Head for valves, bends and other issues | [7 empty] | 10 | ft
There is an elevation difference of | [7 empty] | 13 | ft
[7 empty] | Total | 30.978 | ft
*************************************************************************************
hL = Head loss (feet of fluid)
f = Darcy friction factor (unitless) |  |  |  | 0.2
L = Pipe length (feet) |  |  |  | 22200
D = Inside pipe diameter (feet) |  |  |  | 0.44575
v = Fluid velocity (feet/sec) |  |  |  | 0.54141 |  |  | d = Inside pipe diameter (inches) |  |  | 5.349
Re = Reynolds number (unitless)
g = Gravitational constant (32.2 feet/sec2) |  |  |  | 32.2 |  |  | Q = Volumetric flow rate (gpm) |  |  | 243
d = Inside pipe diameter (inches) |  |  |  | 5.349 |  |  | ρ = Fluid density (lb/ft3) |  |  | 62.4
Q = Volumetric flow rate (gpm) |  |  |  | 243 |  |  | μ = Fluid viscosity (centipoise (cP)) |  |  | 1.002
f = Darcy friction factor (unitless)
hL =( | 0.0311 | f | L | Q | d | ) | ε = Pipe absolute roughness (inch) |  |  | 5e-06
hL =( | 0.0311 | 0.2 | 22200 | 243 | 5.349 | ) | v = Fluid velocity (feet/sec) |  |  | 0.54141
hL = | 53276.7977 | ft |  |  |  |  | Re = | 143322.9469 |  | 551615.3703
[7 empty] | f = | 0.016598
| f | L | D | v | g
hL = | 0.2 | 22200 | 0.44575 | 0.54141 | 32.2
hL = | 45.3369 | ft
f = | 0