## RunOff Calcs
100 Year Rain Event
Long lasting expected rainfall of 1 inches per hour for 5 hours
The main structure has an approximate roof area = |  |  | 50000 | s.f.
| Rainfall Rate | = | 1 | in./hr
| Convert to ft | = | 0.083333 | ft /hr
| Rainfall per hour (roof x rate) | = | 4166.6667 | cu ft/hr
If rainfall is considered constant then estimate flow per second
|  | = | 1.1574 | cfs
The roof has 16 downspouts from the roof therefore each downspout
would effectively handle |  | = | 0.072338 | cfs
Paved area to drain has an approximate area |  | = | 50000 | s.f.
| Rainfall Rate | = | 1 | in./hr
| Convert to ft | = | 0.083333 | ft /hr
| Rainfall per hour (paving x rate) | = | 4166.6667 | cu ft/hr
If rainfall is considered constant then estimate flow per second
|  | = | 1.1574 | cfs
*******************************************************************************
Trough to support 100 Year Rain Event
A trough that is 16" wide would have a depth of |  |  | 0.4 | ft
|  |  | 4.8 | inches
*******************************************************************************
Alternative Rainfall Event
Using an alternative method of calculating rainfall intensity
for short durations, see tab "Alternative Rainfall Calcs
Calcs show average intensity= |  |  | 5.01 | cfs
A trough that is 16" wide would have a depth of |  |  | 0.76 | ft
|  |  | 9.12 | inches
*******************************************************************************
Pipe Calcs
Assume that the pipe is 18" diameter with 1% slope
The depth in the 18" pipe to allow 5.01 cfs flow is |  |  | 0.67 | ft depth
|  |  | 8.04 | inches

## Trough Drain
Manning's Equation
Rectangular Section (Trough Drain)
Slope | n | Base (b) | Depth of Liquid (h) | Area | Pw | Rh | Q | V
ft/ft |  | ft | ft | ft2 | ft | ft | ft3/sec | ft/sec
0.01 | 0.015 | 1.33 | 0.76 | 1.0108 | 2.85 | 0.35467 | 5.0308 | 4.9771
*************************************************************************************************

## Drain Pipe
Circular Section
Slope | n | Riadus | Depth of Liquid | Area | Pw | Rh | Q | V
ft/ft |  | ft | ft | ft2 | ft | ft | ft3/sec | ft/sec
0.01 | 0.011 | 0.75 | 0.67 | 0.7638 | 2.1959 | 0.34783 | 5.1171 | 6.6995
Re = 4VR / v |  |  |  |  | Re = | 269.1641
Re = Reynolds Number (Unitless)
V= average velocity (ft/s)
R = Hydrualic Radius (ft)
v = kinmatic viscosity (ft2/s) |  |  |  | v of water = |  | 0.03463
If the Reynolds number for closed conduits, and is above 4,000; the flow is generally turbulent.

## Alternative Rainfall Calc
Jindal Tubular
Drainage Calculations - Modified Rational Method, LDOTD Hydraulics Manual
Predevelopment Condition
100 Year Frequency
Q= CIA |  |  | Factor | Area, sf | Total | mi^2
C | Undeveloped Area |  | 0.2 |  | 0 | 0
| Gravel Area |  | 0.25 |  | 0
| Building/ Parking |  | 0.95 | 100000 | 95000
|  |  |  | 100000 | 95000
| Weighted C Factor |  | 0.95
I | Hydraulic Length, L | 440 | feet
| Slope, in %, S | 1 |  |  | 0.01
| Runoff Coefficient, C | 0.95
| Time of Concentration | Tc | 8.0936 | minutes
|  | 10.8503 | 1.0597 | 1
| I, intensity from Region 1 |  | 9.7497
| D | 0.13489
| a | 5.487
| b | 0.334
| c | -0.759
| Area, Acres | 2.2957
| Q100 Flow, cfs | C*I*A | 21.263 | cfs
| Q100 Predev Flow | 21.263 | cfs
Postdevelopment Condition
100 Year Frequency
Q= CIA |  |  | Factor | Area, sf | Total
C | Undeveloped Area |  | 0.2 | 40867 | 8173.4
| Gravel Area |  | 0.25 |  | 0
| Building/ Parking |  | 0.95 | 59133 | 56176.35
|  |  |  | 100000 | 64349.75
| Weighted C Factor |  | 0.6435
I | Hydraulic Length, L | 348 | feet
| Slope, in %, S | 0.56
| Runoff Coefficient, C | 0.6435
| Time of Concentration | Tc | 12.8691 | minutes
|  | 9.8978 | 1.6463 | 1.122
| I, intensity from Region 1 |  | 8.6558
| D | 0.21448
| a | 5.487
| b | 0.334
| c | -0.759
| Area, Acres | 2.2957
| Q100 Flow, cfs | C*I*A | 12.787 | cfs
| Q100 Postdev Flow | 12.787 | cfs
| Q100 Allowable Flow- Undeveloped Flow = |  |  |  |  | 21.263 | cfs
Storage Requirements
| Storm Duration |  | i | q, cfs | Max. Storage Volume, cf
| 10 | min | 9.2764 | 13.7037 | -6365.7624
| 20 | min | 7.4586 | 11.0184 | -7744.8082
| 30 | min | 6.2975 | 9.3031 | -10600.1444
| 40 | min | 5.4842 | 8.1017 | -14280.6837
| 50 | min | 4.879 | 7.2076 | -18480.6694
| 60 | min | 4.409 | 6.5133 | -23034.6359
| 75 | min | 3.8701 | 5.7172 | -30323.6692
| 80 | min | 3.7224 | 5.4989 | -32845.4003
| 90 | min | 3.4627 | 5.1153 | -37996.4214
| 100 | min | 3.2415 | 4.7885 | -43266.9362
| 110 | min | 3.0505 | 4.5064 | -48635.024
| Average Rate |  | 5.0138 | 7.4067