## Mini Splits
MIN-SPLIT SCHEDULE
AIR HANDLER | [7 empty] | HEAT PUMP | [7 empty] | MOP | Remarks
Tag | Qty. | Make | Model | Tons (Nominal) | Airflow (CFM) | Power |  | Tag | Make | Model | Cooling (MBH) | Heating (MBH) | Power |  | MCA
[6 empty] | VAC | Ph | [5 empty] | VAC | PH
MS-1 | 1 | Daikin | FCQ24TAVJU | 2 | 568 | 208 | 1 | HP-1 | Daikin | RZQ24TBVJUA | 24 | 27 | 208 | 1 | 17.2 | 20 | 1, 2, 3
MS-2 | 1 | Daikin | FCQ24TAVJU | 2 | 568 | 208 | 1 | HP-2 | Daikin | RZQ24TBVJUA | 24 | 27 | 208 | 1 | 17.2 | 20 | 1, 2, 3
MS-3 | 1 | Daikin | FCQ24TAVJU | 2 | 568 | 208 | 1 | HP-3 | Daikin | RZQ24TBVJUA | 24 | 27 | 208 | 1 | 17.2 | 20 | 1, 2, 3
MS-4 | 1 | Daikin | FCQ24TAVJU | 2 | 568 | 208 | 1 | HP-4 | Daikin | RZQ24TBVJUA | 24 | 27 | 208 | 1 | 17.2 | 20 | 1, 2, 3
MS-5 | 1 | Daikin | FCQ24TAVJU | 2 | 568 | 208 | 1 | HP-5 | Daikin | RZQ24TBVJUA | 24 | 27 | 208 | 1 | 17.2 | 20 | 1, 2, 3
MS-6 | 1 | Daikin | FCQ24TAVJU | 2 | 568 | 208 | 1 | HP-6 | Daikin | RZQ24TBVJUA | 24 | 27 | 208 | 1 | 17.2 | 20 | 1, 2, 3
NOTES:
1 | Cooling capacities to be rated in accordance with AHRI standard 210/290 for ASHRAE standard design weather conditions in New Orleans, LA.
2 | Furnish with wired wall thermostat / controller, condensate pump and spare filter media.
3 | Install units in accordance with manufacturer's recommendations and drawings.