Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

October 15, 2010

Mr. Shelton Grona

Atkin & Associates Builders

P.O. Box 820 

Edna TX, 77957

RE:
ZE 1002093

8605 S. 34th Ave.

Amarillo, TX  

Dear Mr. Grona,

Article 518.4 (B) states that electrical nonmetallic tubing is allowed for Assembly Occupancies with more than 100 occupants in non-rated construction.  Article 362 specifically states the requirements for installation of ENT. 

Although ENT wiring method is not the preferred method, it is allowed for use on subject project.  Installation of ENT wiring must follow the requirements of the NEC.  Specifically note that when using ENT above suspended ceilings, the ceiling must provide a thermal barrier that has at least a 15-minute finish rating as identified in listings of fire-rated assemblies (UL).

Sincerely,

