3rd  Floor

(Note when I say on the Door Schedule or not on the Door Schedule it means a PR is listed for the door in the Remarks Section)

- Door 3011A is listed on the Hardware Schedule (pg 28) and the Door Schedule but can not find it on the IDN Submittal.

- Door 3401A is listed on the Hardware Schedule (pg 37), on the drawing, and the Door Schedule but can not find it on the IDN Submittal.

- Door 3401B & 3401C is listed on the IDN Submittal and the drawing but they are not listed on the Hardware Schedule or the Door Schedule.

- Door 3014A pg 40, of the Hardware Schedule does not show how the locking mechanism that the system is to open.  Is it MAG lock or something else?

- IDN Submittal 3rd floor last page has Door 2600A maybe suppose to be 3600A?

- IDN Submittal 3rd floor page 2 of submittal shows Door 3201C maybe suppose to be 3401C?

- EST5-3 (Existing Stairwell 5) is on the IDN Submittal and drawing, it is not on the Door Schedule or the Hardware schedule.

- ST4-3 is on the IDN Submittal and the drawing, it is not the Door Schedule or the Hardware schedule.

1st floor

- Door 1054B Hardware Schedule calls for 1 proximity reader and uses an exit device on the inside; IDN Submittal calls for 2 proximity reader.  Drawing shows PR on the hinge side of door outside, should be opposite side of hinge.

- Door 1204A could not be found on IDN Submittal.  The drawing shows the PR inside lobby, should be on outside? Drawing shows PR on the hinge side of door, should be opposite side of hinge.

- Door ST3-1 drawing shows the PR inside stairwell, should be on outside?

- Door 1002B which access is being controlled?

- Doors 4246, 5254, 5257 are listed on Hardware Schedule (pg 18) and Door Schedule but can not find them on IDN Submittal.

- Door 1031A AND 1051A area listed on the Hardware Schedule (pg 3) without Access Control.  The Door Schedule list this with PR and the IDN Submittal shows PR, MS and DP.  I need to know how this door is secured, i.e. Electric Strike or Mag Lock.

- Door 1009A & 1221A IDN Submittal shows only 1 PR but the drawing shows 2.

- Door 1011 IDN Submittal shows 1 PR and this matches the drawing.  This door does not have a PR on the Door Schedule nor the Hardware Schedule.

- Door 1316A can not locate on drawing.  This door is to have a PR, MS and DP

- Door 1200A & 1200B, pg 8 of Hardware Schedule does not list access control materials for door.

- Door 1205 is on the Hardware Schedule and the Door Schedule but is not on the IDN Submittal

- ST4-1 is on the IDN Submittal and the drawing, it is not the Door Schedule or the Hardware schedule.

- 1201B is on the IDN Submittal, the drawing, and on the Door Schedule but no access control information is on the Hardware Schedule.

- 1333 is on the IDN Submittal and the drawing, it is not the Door Schedule or the Hardware schedule.

- 1001A is on the IDN Submittal and the drawing, it is not the Door Schedule or the Hardware schedule.

- Door 1051A is not listed on the Hardware Schedule or the Door Schedule.  It is listed on the IDN Submittal and drawing.

- Door 1230A is not listed on the Hardware Schedule or the Door Schedule.  It is listed on the IDN Submittal and drawing.

- Door 1332A & 1332B are not listed on the Hardware Schedule or the Door Schedule.  It is listed on the IDN Submittal and drawing.

- Door 1333A is not listed on the Hardware Schedule or the Door Schedule.  It is listed on the IDN Submittal and drawing.

2ND Floor

- Doors 2011B, 2025, 2012 on the Hardware schedule shows both Electric Strike and Mag Lock?