Additional  Comments not covered by CLA Review:

Question about all of the paging systems.  Do the speakers get wired back to the Access Control Room or do they get directly connected to the amplifier sitting on the reception desk?  If back to the Access Control Room, the microphone you have in the package can have a cable length up to 100 feet in the low-impedance position, however I believe you will need shielded cable.

Building A 1st Floor:

There are 2 PA systems shown on the electrical plans, 1 at the dormitory reception desk and 1 at the nurse station sitting next to the AI Phone System.

You show an AI phone at door HC162a but not the base station at the Nurse Station.

I count 14 exit signs without cameras however you show 13

There are 7 cameras on the electrical plans in the Health Care and 1 camera outside the elevators that do not have a designation “D” or “O”.  My assumption was that these are dome cameras.  Your count for dome cameras, CE-D953, is 8.  Remind me to review this with you because CLA did not comment, I need to clarify that the all of these are dome cameras.

I count 3 faux occupancy, Motion, cameras, Rm A100a, A106 & A117, your count is 2.

Door A171 you show a DPS only however the electrical drawings show a CR as well.

And of course the 9 exterior dome cameras.

Building A 2nd Floor:

Door A264 not on your door list. Should be Mortise Lock VCP 4055 x 626

Building A 3rd  Floor:

Door A302 not on your door list. Should be Mortise Lock VCP 4055 x 626

Building A 4th  Floor:

Door A402 not on your door list. Should be Mortise Lock VCP 4055 x 626

Building A 5th  Floor:

Door A502 not on your door list. Should be Mortise Lock VCP 4055 x 626

These are my input for CLA’s Review::

Door		Comment

HC100b		1.  HC100b is shown as a single door on Architectural Plan.  Electrical Plan shows only 1 reader on door HC100b and nothing on HC100a.

2.  Comment for you

HC100a		1.  HC100a is shown as a single door on Architectural Plan.  Electrical Plan shows only 1 reader on door HC100b and nothing on HC100a.

HC100c		1.  Comment for you

HC161b		1.  The electrical plan shows a pushbutton release at the reception desk for door HC160-a not HC-161b.

BUILDING A

A104a 		1.  Comment for you

2.  Comment for you

A124b 		1.  Comment for you

A104b		The electrical plan does show 2 each readers for this door.

A100e 		1.  Comment for you

A115a 		1.  Comment for you

A108 		1.  Comment for you

A113A 		1.  This room is a H/C  double bedroom, don’t know about hardware.

2.  Comment for you

A200b, A200d	1.  Comment for you

A269A 		1.  Room A269 is a standard double bedroom;  Room A213 is a H/C double bedroom.  The electrical plan shows A213 with a 2ea PB, 1ea CR and 2ea Z

A202 		1.  Room A202 is a H/C double bedroom.  The electrical plan shows A202 with 2ea PB, 1ea CR and 2ea Z

A203a		1.  The plans show this as a lounge.  The electrical plan shows A202 with 2ea PB, 0ea CR and 2ea Z

A213 		1.  See A269A above.

A239 		1.  The plans show this as a single H/C bedroom.  The electrical plan shows A239 with 2ea PB, 1ea CR and 2ea Z

A254a		1.  The plans show this as a lounge.  The electrical plan shows A254 with 2ea PB, 0ea CR and 2ea Z

LUCKY DAY

LD100a		1.  Comment for you

LD116, LD118	1. LD116 is an Elevator.  LD118 is an egress from a stairway shown on our plan SEC-C1.  The electrical plan does not show any PB, CR or Z for door LD118. This is one of the doors we discussed recently.

LD115		1.  LD115 is a double door between the waiting area and the offices.  The electrical plan shows LD115 with 2ea PB, 1ea CR and 2ea Z.  This is one of the doors we discussed recently.

2.  Comment for you

BUILDING B

B100b		1.  Comment for you

B100a		1.  Comment for you

B128a		1.  Comment for you

B103A		1.  B103 is the reception desk with the PA.  Room B130 is an H/C Staff Apt.  The electrical plan shows B130A with 2ea PB, 1ea CR and 2ea Z.  This is one of the doors we discussed recently.

B134A		1.  Comment for you

2.   Comment for you

3.   Comment for you

B149A		1. Comment for you

2.   Comment for you

3.   Comment for you

B126		1.  The plans show this as a lounge.  The electrical plan shows B126 with 2ea PB, 0ea CR and 2ea Z

B200 a / b	1.  Comment for you

B213A		1.  Comment for you

B220		1.  The plans show this as a single H/C bedroom.  The electrical plan shows B220 with 2ea PB, 1ea CR and 2ea Z.  This is one of the doors we recently discussed.

B249A		1.  Comment for you

B253		1. The plans show this as a lounge.  The electrical plan shows B253 with 2ea PB, 0ea CR and 0ea Z.

BUILDING C

C101a		1.  Comment for you

C122b		1.  This is the exterior door to the electrical closet.

C100a		1.  Comment for you

C125A		1.  Comment for you

C131A		1.  Comment for you

C132A		1.  Comment for you

C200a		1.  Comment for you

C213		1.  Comment for you

C320		1.  This is the laundry room

C420		1.  This is the laundry room

C520		1.  This is the laundry room

Building A CCTV

3rd Floor -  	1.  The electrical plans show a faux Smoke Detector with camera outside room A334 and the other one is outside  Room A358.  Your count was for only 1.

4th Floor	1.  The electrical plans show a faux Smoke Detector with camera outside room A434 and the other one is outside  Room A458.  Your count was for only 1.

5th Floor 	1. The electrical plans show a faux Smoke Detector with camera outside room A534 and the other one is outside  Room A558.  Your count was for only 1.

Building B CCTV

1st Floor	1.  I can find only 7 faux Occupancy Sensor Cameras

Building A Paging System

1st Floor	1.  I found 33 speakers on the electrical plans.  It does look like the 2 speakers in the hallway outside HC104 could be combined into one.

2nd Floor	1.  I found 21 speakers on the electrical plans.