## Wind Long Side
Overall Building Size = |  |  | 224 | ft long x | 61 | ft wide
Building mean height (h) = |  |  | 18.39 | ft
a = 10 % of least horizontal dimension or 0.4h; which ever is smaller. But not less than 4% of least horizontal dimension or 3 ft
| 10% of least horizontal dimension = | [5 empty] | 6.1 | ft
| 0.4h = | [5 empty] | 7.356 | ft
| 4% of least horizontal dimension = | [5 empty] | 2.44 | ft
Therefore a = |  | 6.1 | ft
This means that each end of the building carries the loads of A for a distance of 2a
The following are calculations are from MWFRS Wind Loads; (+) numbers act toward and (-) numbers act away from the normal surfaces
| A | B | C | D | E | F | G | H
Loads psf | 55.5 | -14.7 | 37 | -8.1 | -48.1 | -33.5 | -33.5 | -25.4
Length, ft | A: 6.1; B: 6.1; C: 217.9; D: 217.9
Height, ft | A: 11.95; B: 12.89; C: 11.95; D: 12.89
Pressure # | 4045.6725 | -1155.8463 | 96344.485 | -22750.7211 | 0 | 0 | 0 | 0
Each end of the long side of the building will be supporting 1/2 load = | F: 64749.1218; G: #
Shear is calculated using
V = v Σbi
V | A: = total allowable shear capacity of wall (lb)
v | A: = allowable shear capacity per unit length (lb/ft)
Σbi | A: = sum of lengths of full-height sheathing segments
Using 15/32" CDX Plywood, 10d (3" x 0.148" common or 3" x 0.128 galv box nails) and the nail pattern around perimeter of plywood is 4" the pressure available to act in shear (v) is equal to
[7 empty] | 460 | plf of shear
Each interior shear wall is | E: 24; F: linear ft in length
Each exterior shear wall is | E: 36; F: linear ft in length
V interior= | A: 11040; B: # (lb) with one side plywood and; E: 22080; F: # (lb) with plywood each side
V exterior= | A: 16560; B: # (lb) with one side plywood
2 interior shear walls with plywood both sides | E: 44160; F: #
End Wall acting in shear with plywood one side | E: 16560; F: #
|  |  |  | Total = | 60720 | # < | 64749.1218 | #
Add a Drag Strut beam between interior Shear Walls, across the hall.
Transfering load to non used Shear Wall on opposite side of hallway.
There are two shear walls on each side of the building. The total additional load required to be
transferred on the Drag Strut beam = | E: 2014.5609; F: #
Each interior shear wall is | E: 24; F: linear ft in length
Therfore the Drag Strut beam must transfer | E: 83.94; F: plf to the opposite wall on the other
side of the hallway
A single 2x12, 8'-6" long can support only 1,512#; however, double 2x12, 8'-6" long can support 6,952#
Use double 2x12's nailed together along with double 2x12 Simpson hanger and a strap on top of beam.

## Wind Short Side
Overall Building Size = |  |  | 224 | ft long x | 61 | ft wide
Building mean height (h) = |  |  | 18.39 | ft
a = 10 % of least horizontal dimension or 0.4h; which ever is smaller. But not less than 4% of least horizontal dimension or 3 ft
| 10% of least horizontal dimension = | [5 empty] | 6.1 | ft
| 0.4h = | [5 empty] | 7.356 | ft
| 4% of least horizontal dimension = | [5 empty] | 2.44 | ft
Therefore a = |  | 6.1 | ft
This means that each end of the building carries the loads of A for a distance of 2a
The following are calculations are from MWFRS Wind Loads; (+) numbers act toward and (-) numbers act away from the normal surfaces
| A | B | C | D | E | F | G | H
Loads psf | 55.5 | -14.7 | 37 | -8.1 | -48.1 | -33.5 | -33.5 | -25.4
Length, ft | A: 6.1; B: 6.1; C: 54.9; D: 54.9
Height, ft | A: 11.95; B: 12.89; C: 11.95; D: 12.89
Pressure # | 4045.6725 | -1155.8463 | 24274.035 | -5732.0541 | 0 | 0 | 0 | 0
Each Long Side of the building will be supporting full load for the Wind hitting the Short Side= | F: 35207.6079; G: #
Shear is calculated using
V = v Σbi
V | A: = total allowable shear capacity of wall (lb)
v | A: = allowable shear capacity per unit length (lb/ft)
Σbi | A: = sum of lengths of full-height sheathing segments
Using 15/32" CDX Plywood, 10d (3" x 0.148" common or 3" x 0.128 galv box nails) and the nail pattern around perimeter of plywood is 4" the pressure available to act in shear (v) is equal to
[7 empty] | 460 | plf of shear
Each side of the short wall will support 1/2 the wind load | F: 17603.8039; G: #
Calculate the length of long wall needed to support 1/2 the wind load. Divide 1/2 the load by the capacity of the shear wall per linear ft.
|  |  | 17603.8039 | # / | 460 | plf = | 38.2691 | linear ft